## Content
SP MANWEB NETWORK DEVELOPMENT PLAN (PART 2 - SCENARIO HEADROOM REPORTING)
Data workbook April 2024 v1.0 | The objective of the Network Development Plan (Part 2) is to inform stakeholders of future possible headroom (demand and generation) across our distribution network. This will enable connections to locate in the most advantageous areas, identify when and where issues might occur and develop targeted mitigations. This workbook contains detailed tabular outputs relating to our Network Development Plan (Part 2).
NDP documents | Network Development Plan | https://www.spenergynetworks.co.uk/NDP
| NDP Summary document | A summary document to introduce our NDP, summarise the contents, and set out our consultation questions.
| SP Manweb Capacity & Development report | A pdf report and supporting excel datasheet for SP Distribution, covering Parts 1 and 2. That is this document and supporting excel datasheet.
| NDP Methodology Statement | As the methodology is the same, this is a combined document for both our SP Distribution and SP Manweb licence areas.
Scenario Overview | Scenario Range | The scenarios consider the range of Net Zero compliant scenarios developed by us, the Electricity System Operator (ESO), and the Climate Change Committee (CCC). We only consider Net Zero compliant scenarios, as Net Zero is mandatory with relevant legislated targets applied across the UK. This means we discounted two DFES and FES scenarios. Falling Short (FS) scenario does not meet Net Zero and so has been excluded. System Transformation (ST) is unable to meet Scottish Government legislative targets or UK interim emission reduction targets, and so has also been excluded. The remaining two DFES scenarios, two FES scenarios, and five CCC scenarios collectively form the Net Zero compliant scenario range and so determine our low and high scenario.
| Baseline Scenario | Our baseline scenario tracks the bottom of the credible range in SP Manweb, and marginally above in SP Distribution due to Scottish Government targets. This is intentional. By basing our investment plan on the lower end of Net Zero compliant forecasts, we are confident that we are only asking for the minimum investment needed to enable Net Zero, as actual EV and heat pump uptake is unlikely to be lower than this baseline scenario. Where actual levels are higher than this baseline scenario, our plan can adapt across to address the difference providing agile uncertainty mechanisms are in place.
| Low Scenario | Minimum of Net Zero compliant scenario range.
| High Scenario | Maximum of Net Zero compliant scenario range.
| Tab | Contents
Demand | Baseline Scenario | Baseline demand headroom data by primary and grid groups.
| Low Scenario | Minimum demand headroom data by primary and grid groups.
| High Scenario | Maximum demand headroom data by primary and grid groups.
Generation | Baseline Scenario | Baseline generation headroom data by primary and grid groups.
| Low Scenario | Minimum generation headroom data by primary and grid groups.
| High Scenario | Maximum generation headroom data by primary and grid groups.
| Tab | Contents
Substation Location | Substation Locations | Map co-ordinates for the SPM primary and grid substation locations.

## Baseline Scenario (Demand)
Demand Headroom (MW)
Return to Contents |  |  |  | Baseline
| Group Name | Voltage (kV) | Grid / GSP Group | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050
Primary Groups | ABERDYFI T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 4.5918 | 4.6954 | 4.6604 | 4.429 | 4.1909 | 3.8879 | 3.5977 | 3.2911 | 2.9097 | 2.5766 | 2.3654 | 1.706 | 1.1557 | 0.80055 | 1.0412
| ABERGELE T1 / PENSARN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 1.8776 | 2.0791 | 1.881 | 1.1496 | 0.24473 | 0.42094 | -1.885 | -3.132 | -4.4886 | -5.8069 | -6.9631 | -10.6362 | -14.3534 | -14.3081 | -14.0635
| ABERSOCH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.1224 | 1.0824 | 0.9427 | 0.78559 | 0.10493 | -0.41302 | -0.94582 | -1.5472 | -2.282 | -2.934 | -3.5002 | -4.8613 | -6.6634 | -6.8682 | -6.5503
| ABERYSTWYTH T1 / NORTH RD T1 / PARC-Y-LLYN T1 / PARC-Y-LLYN T2 / U C WALES T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 18.5714 | 19.2506 | 19.1187 | 18.0165 | 16.8978 | 15.4907 | 14.089 | 12.5865 | 11.0434 | 9.4933 | 8.2585 | 3.3016 | -3.358 | -5.8026 | -4.5021
| ACER AVE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 0.20408 | 1.0249 | 1.0939 | 1.964 | 4.3225 | 4.186 | 0.77458 | 0.00089688 | -0.81347 | -1.6126 | -2.326 | -5.0376 | -8.4333 | -11.0376 | -10.9895
| ACORNFIELD RD T1 / DICKINSONS T1 / HAMMOND RD T1 / KODAK T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 14.9898 | 15.4094 | 15.4492 | 14.915 | 14.5562 | 14.1042 | 13.7305 | 13.4763 | 13.3658 | 13.1187 | 12.8874 | 11.1833 | 8.4324 | 7.7068 | 8.4006
| ACTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4082 | 2.6257 | 2.5972 | 2.3592 | 2.1036 | 1.7881 | 1.4702 | 1.1224 | 0.7594 | 0.37407 | 0.054845 | -1.2453 | -2.9499 | -3.9905 | -3.5746
| AIGBURTH VALE T1 / IVY AVE T1 / MATHER AVE T1 / MOSSLEY HILL T1 / WAVERTREE T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 18.1429 | 19.3926 | 19.475 | 18.7173 | 17.9867 | 17.1014 | 16.1349 | 15.1049 | 14.0723 | 12.9105 | 11.8942 | 8.1996 | 2.6869 | 0.15171 | -0.51005
| AINSDALE T1 / PINFOLD LA T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 2.6612 | 2.8948 | 2.782 | 2.2527 | 1.6736 | 0.96991 | 0.23828 | -0.57282 | -1.4763 | -2.3371 | -3.0854 | -5.5314 | -8.2806 | -8.8305 | -8.8633
| AINTREE LOCAL T1 / OLD ROAN T1 / WANGO LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 8.0918 | 8.4335 | 8.3528 | 7.5856 | 6.916 | 6.1149 | 5.327 | 4.4909 | 3.7299 | 2.9094 | 2.1557 | -0.89002 | -5.0803 | -6.8198 | -7.4131
| AIRBUS T1 / BROUGHTON RETAIL PARK T1 / MIXALLOY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 12.8469 | 13.0545 | 13.01 | 12.621 | 12.2458 | 11.7793 | 11.3156 | 10.8524 | 10.3731 | 9.8667 | 9.3957 | 7.5078 | 5.0887 | 4.4785 | 4.7372
| AIRPORT T1 / ALDERWOOD AVE (CROYDE RD) T1 / HAREFIELD RD T1 / METAL BOX (SPEKE) T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 19.5408 | 19.7952 | 19.7055 | 19.1733 | 18.6036 | 17.9723 | 17.3587 | 16.7127 | 16.0647 | 15.3686 | 14.6621 | 12.1746 | 8.3268 | 7.4808 | 7.8792
| ALBERT DOCK T1 / KINGS DOCK T1 / KINGS DOCK T2 / WAPPING T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 23.2959 | 23.5075 | 23.5176 | 23.2878 | 23.109 | 22.8869 | 22.7051 | 22.5441 | 22.4258 | 22.2571 | 22.0852 | 21.2586 | 19.8582 | 19.5727 | 19.9735
| ALLERTON T1 / ECP WEST-BANKS RD T1 / GARSTON T1 / WEAVER IND EST T1 / YEW TREE RD T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 22.9694 | 23.5261 | 23.5519 | 23.0241 | 22.5933 | 22.0679 | 21.5894 | 20.8202 | 20.216 | 19.4714 | 18.6987 | 15.8257 | 10.9892 | 9.1876 | 9.5907
| ALMATEX T1 / ST HELENS WWTW T1 / WATERY LA T2 / ex DELTA METALS T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 8.5367 | 8.9039 | 8.8829 | 8.5438 | 8.2351 | 7.8763 | 7.5301 | 7.2063 | 6.8924 | 6.5254 | 6.1547 | 4.6426 | 2.2341 | 1.6873 | 2.1747
| ALMONDS TURN T1 / ATLANTIC COMPLEX T1 / GIRO T1 / MIDLAND BANK T1 / NETHERTON T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 22.6735 | 23.0345 | 22.7325 | 21.7106 | 20.5033 | 19 | 17.4626 | 15.7357 | 13.8385 | 11.8405 | 10.0308 | 2.9076 | -6.1247 | -7.4995 | -6.1882
| ALPOCO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.2755 | 5.3357 | 5.3188 | 5.1905 | 5.0645 | 4.9209 | 4.7748 | 4.6154 | 4.4558 | 4.2964 | 4.1543 | 3.6553 | 3.0438 | 2.9314 | 2.9741
| AMLWCH T1 / AMLWCH T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 6.8469 | 6.7775 | 6.6305 | 6.1869 | 5.6721 | 5.0812 | 4.4708 | 3.7891 | 3.0036 | 2.2753 | 1.6575 | -0.18355 | -2.0992 | -2.2464 | -2.0129
| ANDERTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.6224 | 3.5918 | 3.3998 | 2.8801 | 2.5599 | 2.0285 | 0.71325 | -0.16709 | -1.1999 | -2.1772 | -3.0336 | -5.7757 | -8.9554 | -9.0157 | -8.9089
| APPLETON T1 / HORNSBRIDGE T1 / LUGSDALE T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 3.4694 | 4.1529 | 4.0447 | 3.1655 | 3.4561 | 4.7681 | -0.11072 | -1.3373 | -2.5919 | -3.9187 | -5.0753 | -9.8609 | -16.2257 | -20.5717 | -20.0883
| ARROWE PK HOSP T1 / CHAMPION PLUGS T1 / CHAMPION PLUGS T2 / WOODCHURCH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 20.5612 | 20.7962 | 20.7853 | 20.4098 | 20.1194 | 19.7834 | 19.4683 | 19.2121 | 19.0012 | 18.7141 | 18.414 | 17.0558 | 14.7852 | 14.1617 | 14.6467
| ARUNDEL T1 / GROVE PK T1 / WAVERTREE VALE T1 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 7.1735 | 7.88 | 7.9668 | 7.6922 | 7.4864 | 7.1919 | 6.8812 | 6.5796 | 6.2514 | 5.907 | 5.6764 | 4.7221 | 3.5636 | 3.5261 | 3.9698
| ASH RD T1 / KELLOGGS (WREXHAM) T1 / KELLOGGS (WREXHAM) T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.9388 | 4.3398 | 4.3154 | 3.695 | 3.1951 | 2.6184 | 2.1209 | 1.6755 | 1.3603 | 0.91978 | 0.53019 | -1.4201 | -4.4792 | -5.1749 | -4.2889
| ASSOCIATED LEAD T1 / GREAT BOUGHTON T1 / PIPERS ASH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 7.4898 | 7.9541 | 7.658 | 6.6017 | 5.3498 | 3.8327 | 2.2131 | 0.36719 | -1.6907 | -3.7052 | -5.4825 | -11.499 | -18.2388 | -18.923 | -18.6725
| ASTMOOR IND EST T1 / MACKAMAX T1 / MERSEY RD T1 / PICOW FARM RD T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 18.6939 | 19.0556 | 18.9952 | 18.5397 | 18.2772 | 17.9151 | 17.5908 | 17.3044 | 17.0782 | 16.7949 | 16.4928 | 14.8772 | 12.3143 | 11.1157 | 11.2477
| ATHOL ST T1 / CHISENHALE ST T1 / SANDHILLS LA T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 9.5531 | 9.6966 | 9.6173 | 9.2264 | 8.8141 | 8.5059 | 8.1279 | 7.7259 | 7.3091 | 6.8482 | 6.4027 | 4.8421 | 2.3214 | 1.9137 | 2.4512
| AUDLEM T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.8673 | 3.9957 | 3.9168 | 3.6792 | 3.3708 | 3.0391 | 2.6727 | 2.2535 | 1.7753 | 1.3051 | 0.89304 | -0.26262 | -1.6982 | -1.9868 | -1.6562
| BALA T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.0204 | 4.0431 | 3.9303 | 3.5216 | 3.0583 | 2.5126 | 1.9672 | 1.3516 | 0.60705 | -0.047534 | -0.55458 | -1.9184 | -3.1139 | -3.0159 | -2.6874
| BANASTRE RD T1 / DOVER RD T1 / GRANTHAM CL T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | -1.8898 | 9.5885 | 9.5467 | 8.9156 | 8.2969 | 7.5526 | 6.7673 | 5.907 | 5.0367 | 4.1419 | 3.3023 | 0.25629 | -3.9758 | -5.7786 | -6.5748
| BANGOR HOSP T1 / BANGOR UNIVERSITY T1 / EITHINOG T1 / HIRAEL T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 16.8673 | 17.3639 | 17.3192 | 16.6688 | 16.0833 | 15.3335 | 14.6123 | 13.9046 | 13.2093 | 12.491 | 11.9131 | 9.3516 | 6.2044 | 4.6725 | 5.2666
| BARBAULD ST T1 / HORROCKS LA T1 / WARRINGTON CENTRAL T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 11.1837 | 11.3211 | 11.2368 | 10.806 | 10.3896 | 9.9327 | 9.5111 | 9.0776 | 8.6428 | 8.1487 | 7.6708 | 5.9571 | 3.118 | 2.6067 | 3.32
| BARMOUTH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.0204 | 5.047 | 4.9558 | 4.6955 | 4.3767 | 4.0058 | 3.6261 | 3.1989 | 2.6815 | 2.2114 | 1.8265 | 0.70889 | -0.38203 | -0.20431 | 0.13267
| BARNSTON T1 / GAYTON T1 / IRBY T1 / THINGWALL T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 12.1531 | 12.6991 | 12.3616 | 10.7948 | 9.043 | 6.9463 | 4.7773 | 2.3773 | -0.22951 | -2.7753 | -4.9518 | -12.2405 | -20.3348 | -22.2781 | -22.4534
| BASCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.6224 | 1.8992 | 1.8829 | 1.591 | 1.2793 | 0.90385 | 0.51804 | 0.09711 | -0.32854 | -0.75657 | -1.1363 | -2.5668 | -4.5594 | -5.5751 | -5.5284
| BASS CHARRINGTON T1 / BASS CHARRINGTON T2 / CLIFTON T1 / YKK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 13.8673 | 14.4737 | 14.479 | 13.8432 | 13.2966 | 12.6009 | 11.9534 | 11.3321 | 10.819 | 10.1762 | 9.5725 | 6.7668 | 2.6101 | 0.58637 | 0.96931
| BATTERSBY LA T1 / RYLANDS ELDON ST T2 | 6 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 8.1102 | 8.1603 | 8.1369 | 8.0836 | 8.0498 | 8.0131 | 7.9577 | 7.8747 | 7.7794 | 7.69 | 7.5961 | 7.2942 | 6.8311 | 6.6536 | 6.6983
| BEAUMARIS T1 / BEAUMARIS T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.9739 | 3.9482 | 3.7985 | 3.4163 | 2.9392 | 2.4225 | 1.8958 | 1.2804 | 0.56805 | -0.10258 | -0.7073 | -2.1373 | -4.1951 | -4.4855 | -4.0127
| BEAUMONT ST T1 / DINGLE VALE T1 / LARK LA T1 / MDHB BRUNSWICK DOCK T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 8.7143 | 10.0861 | 9.7141 | 9.3779 | 9.1923 | 8.2848 | 7.9947 | 7.7645 | 7.6636 | 7.4153 | 7.2178 | 5.7191 | 3.2465 | 2.8301 | 3.8442
| BEDBURN DV T1 / BLUEBELL LA T1 / BROOKBRIDGE T1 / ECCLESTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 12.5816 | 13.3043 | 13.0715 | 11.7035 | 10.106 | 8.0886 | 5.9591 | 3.5319 | 0.88921 | -1.8114 | -4.1987 | -13.0293 | -22.6949 | -23.3244 | -22.0593
| BEECH ST T1 / LISTER DV A T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 4.5469 | 4.7749 | 4.8039 | 4.6792 | 4.5983 | 4.4827 | 4.3738 | 4.2759 | 4.2007 | 4.0996 | 4.0036 | 3.5198 | 2.8101 | 2.6312 | 2.7097
| BEMROSE T1 / CARR LA EAST T1 / LUCAS (FAZAKERLEY) T1 / NORRIS GREEN T1 / WEST DERBY T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 17.8163 | 18.7732 | 18.7428 | 17.8012 | 17.0011 | 16.0164 | 14.9827 | 13.941 | 12.9241 | 11.7905 | 10.7481 | 6.7838 | 0.76684 | -2.3425 | -3.0993
| BENTINCK ST T1 / BENTINCK ST T2 / CHESTER ST T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 10.2612 | 10.3122 | 10.1659 | 9.5654 | 8.9782 | 10.1284 | 9.5009 | 8.8322 | 8.1004 | 7.3872 | 6.723 | 4.4192 | 1.3294 | 0.77873 | 0.90657
| BERSHAM COLLIERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 1.602 | 1.6863 | 1.6786 | 1.5372 | 1.4082 | 1.2387 | 1.0621 | 0.89679 | 0.71249 | 0.53636 | 0.38436 | -0.26846 | -1.1133 | -1.5643 | -1.5506
| BERSHAM RD T1 / IND COOPE T1 / RHYD BROUGHTON LA T1 / TUTTLE ST T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 14.1939 | 14.8153 | 14.721 | 13.8895 | 13.1701 | 12.2299 | 11.3002 | 10.3665 | 9.4387 | 8.4909 | 7.7123 | 4.2765 | 0.10376 | -2.38 | -1.4292
| BETHESDA T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 3 | 3.1731 | 3.1226 | 2.8404 | 2.5297 | 2.1306 | 1.729 | 1.3042 | 0.82994 | 0.34929 | -0.031559 | -1.4381 | -3.1023 | -4.1618 | -3.7504
| BETWS-Y-COED T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.9694 | 3.8968 | 3.7365 | 3.2353 | 2.6691 | 2.0132 | 1.3796 | 0.65201 | -0.21886 | -0.98833 | -1.6047 | -3.1464 | -4.7857 | -4.8651 | -4.5861
| BEWSEY T1 / OWEN ST T1 / RODNEY ST T1 / RYLANDS ELDON ST T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 13.8061 | 14.3234 | 14.2777 | 13.5333 | 12.8486 | 12.0455 | 11.2768 | 10.5074 | 9.7709 | 8.9646 | 8.2248 | 5.282 | 0.93179 | -0.22194 | 0.17834
| BIBBYS T1 / INLAND REVENUE OFFICES T1 / REGENT RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 5.6224 | 6.1282 | 6.1519 | 8.1595 | 7.7649 | 7.3738 | 6.9657 | 5.6876 | 5.3745 | 4.988 | 4.6524 | 3.0399 | 0.92388 | 0.48121 | 0.5735
| BICC HUYTON QUARRY T1 / TARBOCK T1 / WHISTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 11.7143 | 11.8798 | 11.7103 | 11.0796 | 10.3303 | 9.4286 | 8.5113 | 7.4742 | 6.3749 | 5.2241 | 4.1635 | 0.12208 | -4.8624 | -5.2381 | -4.7833
| BICC WREXHAM T1 / MARCHWIEL T1 / WIE CENTRAL T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 6.898 | 7.2789 | 7.3074 | 6.8654 | 6.5842 | 6.2315 | 5.9471 | 5.7621 | 5.7099 | 5.5378 | 5.3558 | 4.0186 | 1.7885 | 1.2641 | -22.9798
| BIRKENHEAD CENTRAL T1 / SINGLETON AVE T1 / TRANMERE T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 9.5673 | 9.7948 | 9.7368 | 9.3454 | 8.8776 | 8.4985 | 8.1263 | 7.5841 | 7.0502 | 6.4791 | 5.8851 | 3.6811 | 0.57209 | -0.26798 | -0.1315
| ex BIXTETH ST T1 / LITTLEWOODS T1 / PALL MALL T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 3.8633 | 3.9715 | 3.9258 | 3.7187 | 3.4693 | 3.2141 | 2.9552 | 2.6844 | 2.4034 | 2.0812 | 1.7607 | 0.70724 | -1.0602 | -1.3276 | -0.87567
| BLACON T1 / COCOA BARRY T1 / CRANE BANK T1 / KNUTSFORD WAY T1 / TOWER WHARF T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 16.2245 | 17.0705 | 16.993 | 16.0245 | 15.091 | 13.8883 | 12.7012 | 11.4745 | 10.3116 | 9.0481 | 7.9512 | 2.9866 | -3.492 | -7.5034 | -6.3265
| BLAENAU FFESTINIOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.6939 | 1.7945 | 1.7716 | 1.6491 | 1.5194 | 1.3468 | 1.1739 | 0.98944 | 0.78203 | 0.57317 | 0.40677 | -0.26892 | -0.9166 | -1.2601 | -0.92045
| BLUNDELL ST T1 / ROPEWALKS T1 / ST JAMES T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 9.0198 | 9.4276 | 9.4701 | 9.2325 | 9.0902 | 8.8885 | 8.723 | 8.6236 | 8.6088 | 8.5213 | 8.4313 | 7.6166 | 6.2072 | 5.8705 | 6.3598
| BLUNDELLSANDS (NORTH) T1 / BLUNDELLSANDS (SOUTH) T1 / CROSBY T1 / KERSHAW AVE T1 / WATERLOO T2 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 15.9898 | 16.8645 | 16.5027 | 14.999 | 13.1904 | 10.958 | 8.5995 | 5.9389 | 3.007 | 0.0033533 | -2.6363 | -12.1456 | -23.1013 | -24.9578 | -23.5844
| BODFARI PRODUCERS T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.6122 | 4.7189 | 4.7298 | 4.6451 | 4.5911 | 4.5137 | 4.4598 | 4.4059 | 4.3906 | 4.35 | 4.3031 | 3.9994 | 3.4633 | 3.2851 | 3.4067
| BOLTON ST T1 / GREEK ST T1 / HPO COPPERAS HILL T1 / OLDHAM PLACE T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.8061 | 5.322 | 5.3686 | 4.8722 | 4.5729 | 4.1868 | 3.8984 | 3.6806 | 3.5769 | 3.3783 | 3.1691 | 1.7763 | -0.50424 | -1.0937 | -0.4975
| BOOTLE GRID T1 / KELLOGGS T1 / PACIFIC RD T1 / WASHINGTON ST T1 / WATERLOO T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | 18.4388 | 19.0863 | 19.0625 | 18.1407 | 17.3505 | 16.3744 | 15.4431 | 14.4966 | 13.6885 | 12.7763 | 11.9545 | 8.1682 | 3.2825 | 1.9062 | 1.7232
| BOOTLE GRID T2 / ORRELL MOUNT T1 / SCARISBRICK AVE T1 / TATTON RD T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | 14.4082 | 15.1102 | 15.0068 | 14.1783 | 13.4239 | 12.5305 | 11.5774 | 10.5425 | 9.5051 | 8.3922 | 7.3383 | 3.4999 | -2.0912 | -4.3621 | -4.7933
| BOTWNNOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.2041 | 5.2757 | 5.2386 | 5.0684 | 4.8752 | 4.6561 | 4.4271 | 4.18 | 3.888 | 3.6321 | 3.4388 | 2.8715 | 2.1685 | 1.8551 | 1.9124
| BOULEVARD T1 / CHAPELFORD T1 / HAWLEYS LA T1 / WESTBROOK T1 / WINWICK QUAY T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 16.2857 | 17.0362 | 16.9741 | 15.9736 | 15.0498 | 13.908 | 12.8038 | 11.7103 | 10.7267 | 9.6012 | 8.5817 | 4.1822 | -2.1246 | -5.6333 | -5.2446
| BOW ST T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.6735 | 2.8102 | 2.7048 | 2.3107 | 1.8162 | 1.6302 | 0.6699 | -0.014426 | -0.75819 | -1.4864 | -2.1373 | -4.213 | -6.5414 | -6.9139 | -6.7467
| BOWATER CONTAINERS T1 / ELLESMERE PORT LOCAL T1 / HH ROBERTSONS T1 / MOBIL OIL (E PORT) T1 / WHITBY T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 6.9082 | 7.5628 | 7.491 | 6.5913 | 5.9128 | 5.032 | 4.2098 | 3.4165 | 2.6681 | 1.8516 | 1.0952 | -2.2152 | -7.1578 | -9.4975 | -9.9555
| BR STATION T1 / DUCHY RD T1 / ELECTRA WAY T1 / MIDLAND ROLLMAKERS T1A / NORTH WESTERN MILLS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 12.7347 | 13.4245 | 8.3114 | 7.1533 | 6.2604 | 1.02 | -0.045426 | -1.0696 | -1.9647 | -2.9807 | -3.9671 | -8.7727 | -15.3189 | -18.3967 | -17.4973
| BRD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.1327 | 2.2712 | 2.2152 | 1.8347 | 1.4547 | 0.99691 | 0.54103 | 0.053123 | -0.45382 | -0.9498 | -1.358 | -3.2613 | -6.3264 | -6.4303 | -6.3014
| BRITISH ALUMINIUM LATCHFORD T1 / GREENHALL WHITLEY T1 / LATCHFORD T1 / LATCHFORD T2 / THAMES BOARD MILL T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 11.8367 | 12.7118 | 12.7782 | 12.1513 | 11.655 | 11.0288 | 10.4127 | 9.8525 | 9.3878 | 8.7955 | 8.272 | 5.7763 | 1.9924 | 0.6271 | 0.80638
| BRITISH OXYGEN T1 / WINDLEHURST T1 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 2.8041 | 3.1316 | 3.4826 | 3.5885 | 2.6338 | 2.3589 | 2.0608 | 0.20406 | -0.14612 | -0.53873 | -0.90969 | -2.1509 | -4.1886 | -4.8133 | -4.5912
| BRITISH PIPE ASSOCIATION T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 3.9388 | 4.0355 | 4.0263 | 3.8903 | 3.7725 | 3.617 | 3.4949 | 3.3954 | 3.3077 | 3.1829 | 3.0672 | 2.5425 | 1.659 | 1.4776 | 1.6927
| BRITISH SIDAC T1 / SHERDLEY RD T1 / ST HELENS LINKWAY T1 / WATERY LA T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 9.6592 | 9.8972 | 9.7723 | 21.0479 | 20.4633 | 19.728 | 19.0107 | 18.2448 | 17.4579 | 16.6504 | 15.9481 | 12.9201 | 9.2033 | 6.2731 | 7.238
| BROADGREEN T1 / CROXTETH T1 / EAST PRESCOT RD (FINCH LA) T1 / KNOTTY ASH T1 / LEYFIELD RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 12.102 | 13.6078 | 13.7149 | 12.77 | 11.948 | 10.9008 | 9.8035 | 8.6716 | 7.6212 | 6.4025 | 5.3115 | 0.95002 | -5.5501 | -8.5093 | -9.1356
| BROMFIELD T1 / BROMFIELD T2 / PONTERWYL T1 / RHYD-Y-GOLEU T1 / SYNTHITE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 22.1224 | 22.7348 | 22.6305 | 21.6112 | 20.6114 | 19.3745 | 18.1337 | 16.8104 | 15.4724 | 14.1119 | 12.9619 | 8.6147 | 3.2234 | 0.35243 | 0.0086098
| BROOK LA T1 / MANNINGS LA T1 / NEWTOWN CHESTER T1 / UPTON HEATH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 12.1327 | 13.0414 | 12.8734 | 11.9121 | 10.9252 | 9.6426 | 8.2538 | 6.7316 | 5.1102 | 3.4748 | 2.0342 | -3.519 | -9.8452 | -13.7626 | -13.01
| BROOK ST T1 / KINGSWAY TUNNEL T1 / NWWA SANDON DOCK T1 / NWWA SANDON DOCK T2 | 11 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 17.1224 | 17.4849 | 17.49 | 17.0292 | 16.68 | 16.3639 | 16.0629 | 15.8198 | 15.675 | 15.4432 | 15.1886 | 13.7507 | 11.4267 | 10.8917 | 11.3679
| BRYN STANLEY T1 / DENBIGH T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.2857 | 4.4472 | 4.3772 | 3.9621 | 3.5486 | 3.0393 | 2.5104 | 1.9663 | 1.3823 | 0.79187 | 0.2849 | -1.6311 | -4.0332 | -4.9788 | -4.8435
| BUCKINGHAM ST T1 / EVERTON RD T1 / SUBURBAN RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 8.6633 | 9.221 | 9.3161 | 9.1642 | 9.0786 | 8.9061 | 8.7862 | 8.6882 | 8.6608 | 8.5755 | 8.4978 | 7.9059 | 7.0419 | 6.9425 | 7.2747
| BUCKLEY T1 / BUCKLEY T2 / BUCKLEY CROSS T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 8.4694 | 8.9653 | 8.8543 | 8.0374 | 7.1774 | 6.126 | 5.0481 | 3.8529 | 2.6637 | 1.4437 | 0.38679 | -3.5705 | -8.514 | -11.3803 | -11.7923
| BUILDWAS RD T1 / MORGAN REFRACTORIES T1 / NESTON MAIN T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 11.1735 | 11.2759 | 11.0434 | 10.1695 | 9.1646 | 7.9928 | 6.7974 | 5.4503 | 3.9899 | 2.5526 | 1.312 | -2.7953 | -7.3816 | -7.5949 | -7.4217
| BURLINGTON AVE T1 / FRESHFIELD T1 / MARSH BROWS T1 / SOUTHPORT RD T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 13 | 13.5936 | 13.4215 | 12.3469 | 11.2102 | 9.8356 | 8.3983 | 6.831 | 5.25 | 3.6168 | 2.1806 | -3.022 | -9.4521 | -13.2276 | -13.6262
| BURMAH OIL T1 / CABOT CARBON T1 / VAN LEER NO 1 T1 | 7 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 1.7673 | 1.9047 | 1.9159 | 1.776 | 1.6727 | 1.5452 | 1.455 | 1.3824 | 1.3641 | 1.3018 | 1.2415 | 0.75809 | -0.076011 | -0.33285 | -0.11709
| BUTLINS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.5306 | 4.661 | 4.6772 | 4.5891 | 4.5323 | 4.448 | 4.3715 | 4.3142 | 4.2699 | 4.1956 | 4.137 | 3.8159 | 3.3189 | 3.1286 | 3.289
| BUTTINGTON CROSS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.398 | 3.5391 | 3.5269 | 3.3546 | 3.2344 | 3.0666 | 2.9166 | 2.785 | 2.6674 | 2.5338 | 2.4038 | 1.7397 | 0.80071 | 0.48639 | 0.53043
| BXL BROMBOROUGH T1 / TULIP T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 3.2551 | 3.4041 | 3.3961 | 3.0591 | 2.8179 | 2.5143 | 2.2508 | 2.0213 | 1.8407 | 1.6244 | 1.4127 | 0.31911 | -1.1869 | -1.4749 | -1.2715
| CABLE ST T1 / GRADWELL ST T2 / OLDHAM PLACE T2 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 5.6837 | 6.222 | 6.2889 | 5.8874 | 5.6385 | 5.3409 | 5.1166 | 4.9535 | 4.6926 | 4.5218 | 4.0954 | 2.1059 | -1.1539 | -1.0965 | -0.14953
| CABLE ST T2 / CROWN COURTS T1 / GRADWELL ST T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 10.2653 | 10.3968 | 10.2803 | 9.6591 | 9.291 | 8.7991 | 8.3172 | 7.8636 | 7.4142 | 6.9191 | 6.4339 | 4.7639 | 2.2138 | 2.2456 | 3.1954
| CADBURYS KRONOSPAN T1 / CADBURYS KRONOSPAN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.6531 | 3.8505 | 3.7881 | 3.4444 | 3.095 | 2.663 | 2.2333 | 1.7911 | 1.3332 | 0.84719 | 0.42227 | -1.203 | -3.3469 | -3.504 | -3.1481
| CADBURYS T1 / CADBURYS T2 / HOPFIELD RD T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 8.7551 | 9.2658 | 9.2688 | 8.8454 | 8.5448 | 8.1483 | 7.7617 | 7.3832 | 7.0493 | 6.6594 | 6.3169 | 4.7114 | 2.4001 | 1.6496 | 1.8762
| CAERGEILIOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5 | 3.5319 | 3.4243 | 3.0548 | 2.5253 | 2.0444 | 1.5445 | 0.81672 | -0.012176 | -0.81873 | -1.57 | -3.9002 | -6.6807 | -7.2958 | -7.0639
| CAERGWRLE T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 1.5816 | 1.7758 | 1.6795 | 1.3363 | 2.3113 | 2.4185 | -1.0555 | -2.0191 | -3.0852 | -4.165 | -5.1352 | -8.2258 | -11.8443 | -12.4591 | -12.1503
| CAERNARFON T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 1.9592 | 2.1204 | 2.0757 | 1.7836 | 1.464 | 1.0958 | 0.7367 | -0.073456 | -0.806 | -1.5832 | -2.3443 | -4.9936 | -8.2418 | -8.6225 | -8.2849
| CAERSWS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 4.3469 | 4.4511 | 4.407 | 4.1632 | 3.8868 | 3.5647 | 3.2218 | 2.8621 | 2.4391 | 2.0589 | 1.7439 | 0.72959 | -0.51855 | -0.79815 | -0.74157
| CALDY T1 / HOYLAKE T1 / MEOLS T1 / WEST KIRBY SOUTH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 14.6531 | 15.1977 | 15.0053 | 13.6966 | 12.4428 | 10.8441 | 9.2719 | 7.6215 | 5.7556 | 4.0259 | 2.7122 | -1.7953 | -6.9589 | -10.5381 | -10.5301
| CARBORUNDUM T1 / HOUGHTONS LA T1 / RAINFORD T1 / WINDLEHURST T2 | 11 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 12.8469 | 13.5638 | 13.4242 | 12.3248 | 11.1613 | 9.7506 | 8.3074 | 6.7511 | 5.1892 | 3.5582 | 2.1271 | -3.4933 | -10.8454 | -15.5879 | -15.5776
| CARLTON ST T1 / CARLTON ST T2 / CHALON WAY T2 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 8.2 | 8.5116 | 8.4886 | 8.0253 | 7.6581 | 7.1978 | 6.7814 | 6.3967 | 6.0332 | 5.6456 | 5.3146 | 3.7503 | 1.5271 | 0.70349 | 0.78405
| CARMEL T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.051 | 1.1827 | 1.1194 | 0.95707 | 0.70611 | 0.42435 | 0.11298 | -0.26258 | -0.69507 | -1.1308 | -1.5322 | -2.7486 | -4.2254 | -4.2818 | -3.9053
| CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 11 | CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 16.9592 | 17.9007 | 17.9095 | 16.8407 | 15.9052 | 14.732 | 13.5755 | 12.4004 | 11.2208 | 10.0009 | 9.0038 | 5.2538 | 0.10686 | -2.1492 | -2.7243
| CEFN MAWR T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.9388 | 3.9891 | 3.8488 | 3.417 | 2.8902 | 2.2989 | 1.6878 | 1.0013 | 0.17125 | -0.59584 | -1.2501 | -3.0402 | -5.1414 | -5.7333 | -5.9245
| CEMAES BAY T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 2.2959 | 2.2827 | 2.1963 | 1.9761 | 1.7134 | 1.4238 | 1.112 | 0.76263 | 0.35786 | -0.012856 | -0.34525 | -1.276 | -2.3409 | -2.4953 | -2.35
| CEMMAES RD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.4898 | 1.5321 | 1.4572 | 1.0755 | 0.70339 | 0.3514 | -0.18676 | -0.67694 | -1.2645 | -1.7703 | -2.1646 | -3.4482 | -4.6355 | -4.9647 | -5.4786
| CEREAL PARTNERS T1 / LEVER GEORGIA AVE T1 / POOL LA T1 / UML LEVER BROMBOROUGH T2 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 20.6224 | 20.893 | 20.9103 | 20.5851 | 20.3486 | 20.0506 | 19.8168 | 19.6439 | 19.5521 | 19.3669 | 19.1866 | 18.0791 | 16.1788 | 15.5264 | 15.8643
| CHALON WAY T1 / TECHNOLOGY CAMPUS T1 / WOODVILLE ST T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 1.5898 | 2.7356 | 2.7027 | 2.2857 | 1.9021 | 1.4502 | 1.0121 | 0.56577 | 0.14548 | -0.3161 | -0.75657 | -2.5703 | -5.0929 | -6.1193 | -6.5416
| CHESHIRE GREEN T1 / NWF T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 4.3265 | 4.4409 | 4.3817 | 4.0581 | 3.8147 | 3.511 | 3.2209 | 2.9663 | 2.7254 | 2.4645 | 2.2141 | 1.05 | -0.58533 | -1.2413 | -1.082
| CHESTER GATES T1 / UNILEVER DUNKIRK T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 4.2245 | 17.8703 | 17.8689 | 17.6194 | 17.4238 | 17.1701 | 16.9711 | 16.567 | 16.4094 | 16.2273 | 16.0646 | 15.2792 | 14.1221 | 13.735 | 13.9133
| CHESTER ST (WREXHAM) T1 / EAGLES MEADOW T1 / RHOSNESNI T1 / WHITEGATE T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 16.2143 | 16.8242 | 16.7066 | 15.9161 | 15.1064 | 14.0619 | 12.9884 | 11.852 | 10.6722 | 9.4928 | 8.5148 | 4.4671 | -0.29409 | -3.4826 | -2.7749
| CHILDWALL T1 / CHILDWALL FIVEWAYS T1 / LYNDENE RD T1 / MIDDLEMASS HEY T1 / NAYLORS RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 13.4898 | 14.7165 | 14.6661 | 13.601 | 12.5226 | 11.1113 | 9.6997 | 8.2089 | 6.6902 | 5.0882 | 3.7545 | -1.8388 | -9.1069 | -14.29 | -12.8237
| CHOWLEY T1 / CHOWLEY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.2143 | 3.4807 | 3.4253 | 2.9986 | 2.5419 | 1.9955 | 1.4263 | 0.80565 | 0.17708 | -0.45869 | -0.99305 | -3.0205 | -5.6266 | -6.9709 | -6.9501
| CHURCH LA T1 / NANT HALL T1 / PRESTATYN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 10.5102 | 10.8644 | 10.7118 | 9.9573 | 9.1051 | 8.0654 | 6.998 | 5.7923 | 4.4702 | 3.2201 | 2.1698 | -1.2073 | -4.6258 | -5.0413 | -4.8896
| CHURCH LAWTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.7347 | 3.8988 | 3.806 | 3.4847 | 3.177 | 2.7721 | 2.3453 | 1.8622 | 1.328 | 0.81876 | 0.35234 | -1.2987 | -3.1352 | -4.3149 | -4.4513
| CHURCH ST WINSFORD T1 / OVER T1 / WHARTON PK T1 / WOODFORD PK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 11.8061 | 12.5961 | 12.495 | 11.4093 | 10.2878 | 8.8851 | 7.4608 | 5.9591 | 4.4012 | 2.8504 | 1.572 | -3.4114 | -9.5037 | -13.3953 | -13.0161
| CIVIC CENTRE T1 / CLAUGHTON AVE T1 / ELECTRICITY ST T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.4147 | 12.4111 | 12.0839 | 11.0935 | 10.5274 | 9.7646 | 8.9589 | 8.087 | 7.1683 | 6.3863 | 5.542 | 1.9874 | -2.772 | -5.3134 | -5.8318
| CLEDFORD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.4184 | 1.8284 | 1.8503 | 1.6106 | 1.3907 | 1.1129 | 0.79721 | 0.47175 | 0.13383 | -0.2291 | -0.54543 | -1.7467 | -3.4376 | -4.6528 | -4.6346
| CLOCKFACE T1 / GEC ST HELENS T1 / HILLS MOSS T1 / NCB SUTTON MANOR T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 16.898 | 17.2855 | 17.1829 | 16.4675 | 15.7609 | 14.8824 | 14.0309 | 13.175 | 12.3391 | 11.4213 | 10.6241 | 7.1223 | 2.3572 | -0.85219 | -0.10779
| CLUBMOOR T1 / DUNLOPS WALTON T1 / WALTON T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 10.1531 | 10.3547 | 10.3656 | 10.1032 | 9.9348 | 9.7701 | 9.6234 | 9.5158 | 9.4743 | 9.3682 | 9.2633 | 8.5542 | 7.3616 | 7.0595 | 7.3839
| CLUBMOOR T2 / LISTER DV A T1 / SUBURBAN RD T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 6.5202 | 7.0173 | 7.0739 | 6.8211 | 6.6172 | 6.352 | 6.0955 | 5.6041 | 5.4039 | 5.141 | 4.9043 | 3.7626 | 2.0907 | 1.7519 | 2.0089
| COEDPOETH T1 / COEDPOETH T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.4592 | 4.6088 | 4.4819 | 4.0561 | 3.528 | 3.9215 | 2.2338 | 1.4813 | 0.64659 | -0.15698 | -0.84801 | -3.2986 | -5.4569 | -4.5284 | -3.6191
| COLWYN BAY T1 / COLWYN BAY T2 / RHOS-ON-SEA T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 11.2041 | 11.5086 | 11.5046 | 11.1959 | 10.9368 | 10.6134 | 10.2797 | 9.961 | 9.6426 | 9.2848 | 8.9622 | 7.3723 | 4.0045 | 3.2844 | 3.29
| CONEY GREEN T1 / OSWESTRY T2 / OSWESTRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 8.3571 | 9.3321 | 9.3444 | 9.0119 | 8.6467 | 8.1445 | 7.5777 | 6.9525 | 6.2326 | 5.5086 | 4.9491 | 2.7799 | 0.10001 | -2.1122 | -1.5163
| CONIX T1 / CONIX T2 / MEDEVA T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 12.6939 | 12.9104 | 12.9215 | 12.6892 | 12.5294 | 12.3374 | 12.181 | 12.0845 | 12.0497 | 11.959 | 11.8571 | 11.0897 | 9.7776 | 9.4076 | 9.7579
| CONNAHS QUAY LOCAL T1 / CONNAHS QUAY LOCAL T2 / HAWARDEN T1 / KING GEORGE ST T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 12.9898 | 13.8699 | 13.7527 | 12.7421 | 11.6636 | 10.294 | 8.8854 | 7.37 | 5.762 | 4.1306 | 2.7654 | -2.2505 | -8.7328 | -13.4581 | -13.3348
| CONWY T1 / DEGANWY T1 / LLANDUDNO JUNCTION T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 14.9731 | 15.528 | 15.3246 | 14.3108 | 13.1329 | 11.6911 | 10.2072 | 8.5389 | 6.6027 | 4.7716 | 3.2425 | -1.7491 | -6.8192 | -6.9664 | -7.0036
| CORWEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.551 | 3.6323 | 3.5591 | 3.202 | 2.8386 | 2.3986 | 1.9712 | 1.5064 | 1.005 | 0.53395 | 0.13881 | -1.2695 | -2.8266 | -3.4787 | -3.6453
| CREWE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.3469 | 2.9122 | -3.1059 | -3.0957 | -3.0957 | -3.1389 | -3.2083 | -3.3043 | -3.4112 | -3.5374 | -3.6283 | -4.6981 | -6.218 | -5.8454 | -5.4707
| CRIGGION RADIO STATION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.1939 | 2.2246 | 2.1976 | 2.098 | 1.9913 | 1.8713 | 1.7592 | 1.6353 | 1.5202 | 1.3876 | 1.2657 | 0.82129 | 0.19327 | 0.033975 | 0.1401
| CROSSFIELDS T1 / CROSSFIELDS T2 / LEVERS CROSSFIELDS T3 / GATEWARTH SEWAGE T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 21.6122 | 22.0566 | 22.1159 | 21.9093 | 21.7566 | 21.5468 | 21.3542 | 21.1777 | 21.0619 | 20.871 | 20.6993 | 19.7916 | 18.3602 | 17.9925 | 18.2953
| CROWTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 3.6531 | 3.8364 | 3.8207 | 3.5988 | 3.355 | 3.0739 | 2.7704 | 2.4423 | 2.1134 | 1.7681 | 1.4629 | 0.38491 | -1.0703 | -1.7857 | -1.875
| CWM DYLI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.6633 | 2.6703 | 2.6453 | 2.5134 | 2.3987 | 2.2449 | 2.1072 | 1.9749 | 1.8038 | 1.6697 | 1.5975 | 1.3959 | 1.2743 | 1.2093 | 1.2675
| DAILY POST & ECHO T1 / DAILY POST & ECHO T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.6286 | 5.1162 | 5.2317 | 5.2386 | 5.2694 | 5.3318 | 5.3516 | 5.3684 | 5.3858 | 5.4066 | 5.4033 | 5.4072 | 5.3329 | 5.3256 | 5.4242
| DARESBURY NPL T1 / DARESBURY NPL T2 / DARESBURY PK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 4.7143 | 4.8218 | 4.7602 | 4.4614 | 4.1498 | 3.7912 | 3.4426 | 3.0812 | 2.7166 | 2.3343 | 1.975 | 0.63459 | -1.2068 | -1.7987 | -1.672
| DAVY WAY T1 / LLAY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.0102 | 2.2653 | 2.2582 | 1.9316 | 1.6549 | 1.3119 | 0.98538 | 0.68485 | 0.41728 | 0.10346 | -0.16629 | -1.4535 | -3.3669 | -4.3688 | -4.0888
| DEESIDE ALUMINIUM T1 / DUNLOP PLASTICS T1 / FIRESTONE T1 / TETRAPAK T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.898 | 3.7382 | 3.8036 | 2.9451 | 2.3594 | 1.6241 | 1.0406 | 0.62513 | 0.48243 | 0.080047 | -0.3278 | -3.1949 | -8.044 | -9.3404 | -8.0072
| DEESIDE IND PK T1 / DEESIDE IND PK 6TH AVE T1 / RAF SEALAND T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 7.2041 | 7.5403 | 7.4749 | 6.9303 | 6.391 | 5.7695 | 5.1878 | 4.6143 | 4.0809 | 3.4577 | 2.8504 | 0.29084 | -3.197 | -3.6487 | -2.8694
| DELAMORE ST T1 / KIRKDALE T1 / WALTON T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 4.6755 | 5.7061 | 5.8519 | 5.5242 | 7.8153 | 7.3915 | 6.9747 | 5.7141 | 5.2832 | 4.7939 | 4.3847 | 2.6659 | 0.48594 | -0.11109 | -0.3606
| DESOTO RD T1 / MERSEY BRIDGE T1 / PITT ST T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 14.4898 | 14.7189 | 14.744 | 14.5801 | 14.4694 | 14.3333 | 14.2203 | 14.1338 | 14.0905 | 14.0154 | 13.9319 | 13.394 | 12.4879 | 12.296 | 12.575
| DIBBINSDALE T1 / PLYMYARD T1 / WIBP HARDKNOTT RD T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 8.7857 | 9.0117 | 8.8507 | 8.1009 | 7.341 | 6.4366 | 5.5116 | 4.5382 | 3.5251 | 2.4596 | 1.4885 | -2.1297 | -6.6262 | -7.5773 | -7.0505
| DINGLE T1 / GRANBY T1 / ST JAMES T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 11.9898 | 12.3045 | 12.3458 | 12.1924 | 12.0808 | 11.9369 | 11.7929 | 11.6729 | 11.5732 | 11.446 | 11.3455 | 10.7911 | 9.9765 | 9.7736 | 9.9146
| DITTON T1 / GAVIN RD T1 / HOUGH GREEN T1 / RTZ T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 12.5204 | 13.1537 | 13.028 | 12.0776 | 11.1167 | 9.9145 | 8.7093 | 7.4896 | 6.2733 | 4.967 | 3.8132 | -1.0114 | -7.5239 | -12.0445 | -11.0446
| DODDS LA T1 / HOLBORN HILL T1 / MAGHULL T1 / MAGHULL T2 / ROBBINS BRIDGE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 13.4898 | 15.3436 | 15.2416 | 13.9456 | 12.3753 | 10.409 | 8.2418 | 5.7508 | 3.0624 | 0.40973 | -1.8284 | -9.7985 | -19.4565 | -26.5301 | -26.751
| DOLGARROG T1 / DOLGARROG T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.051 | 3.0807 | 2.982 | 2.6114 | 2.1929 | 1.725 | 1.2597 | 0.74542 | 0.16323 | -0.37773 | -0.84332 | -2.1868 | -3.8622 | -4.2201 | -3.8779
| DOLGELLAU T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.4082 | 3.4772 | 3.3554 | 2.8779 | 2.3746 | 1.7561 | 1.1467 | 0.47306 | -0.3623 | -1.0775 | -1.6002 | -3.0215 | -4.1815 | -4.0398 | -3.8232
| DUCKINGTON T1 / DUCKINGTON T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.8418 | 4.952 | 4.8483 | 4.4413 | 3.9778 | 3.4635 | 2.8974 | 2.2819 | 1.5886 | 0.92323 | 0.33302 | -1.6283 | -3.82 | -4.0579 | -3.8491
| DUDDON T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 5.3061 | 5.3735 | 5.3594 | 5.2088 | 5.068 | 4.9042 | 4.7344 | 4.5622 | 4.3851 | 4.2065 | 4.05 | 3.4213 | 2.5779 | 2.1828 | 2.161
| DYFFRYN ARDUDWY T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.3265 | 5.2745 | 5.1965 | 4.8487 | 4.4944 | 4.0786 | 3.6762 | 3.2334 | 2.733 | 2.2989 | 1.9801 | 1.0547 | 0.22861 | 0.15203 | 0.035185
| DYSERTH RD T1 / FFORDD LAS T1 / FFORDD LAS T2 / WESTBOURNE AVE T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 10.9082 | 12.5812 | 12.6986 | 12.0571 | 11.3236 | 10.2659 | 9.1458 | 7.8682 | 6.4145 | 5.0733 | 4.1328 | 0.7596 | -2.6039 | -5.4359 | -4.7665
| EDEN VALE T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.0306 | 3.2421 | 3.23 | 3.0151 | 2.7766 | 2.4948 | 2.2023 | 1.8844 | 1.5581 | 1.2257 | 0.92714 | -0.44297 | -3.0702 | -3.3611 | -3.165
| EDERN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 0.84694 | 0.75327 | 1.0497 | 0.43759 | 0.17428 | 0.13091 | -1.7596 | -2.5031 | -3.3965 | -4.181 | -4.8194 | -6.5336 | -8.2308 | -8.4144 | -8.1652
| EDGE HILL T1 / LIVERPOOL UNIVERSITY T1 / LIVERPOOL UNIVERSITY T2 / LIVERPOOL UNIVERSITY T3 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 13.6837 | 14.2017 | 14.1812 | 13.5916 | 13.057 | 12.4274 | 11.8652 | 11.3255 | 10.8621 | 10.2702 | 9.6629 | 7.1854 | 3.0655 | 2.2965 | 3.3049
| EDGE LA (TAPLEY PLACE) T1 / LISTER DV B T3 / MILL LA (WAVERTREE) T1 / PLESSEY (EDGE LA) T1 / STONEYCROFT T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 16.449 | 18.3813 | 18.7143 | 18.5803 | 18.4242 | 18.204 | 17.8619 | 17.4411 | 17.0204 | 16.5144 | 16.1213 | 14.4399 | 12.1058 | 12.3353 | 13.4101
| EGA ELECTRIC T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4 | 4.0578 | 3.9923 | 3.722 | 3.4373 | 3.1141 | 2.7749 | 2.4168 | 2.018 | 1.6187 | 1.2799 | 0.12342 | -1.1933 | -1.3504 | -1.1902
| EGERTON T1 / ROCK FERRY T1 / SHELL TRANMERE T1 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | 5.602 | 6.0732 | 5.9931 | 5.3662 | 4.8955 | 4.3428 | 3.7967 | 3.2565 | 2.7127 | 2.105 | 1.5384 | -0.66294 | -3.999 | -5.0031 | -4.7463
| EGREMONT T1 / LISCARD T1 / POULTON T1 / STONE MANGANESE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 13.2857 | 14.2545 | 14.3957 | 14.0137 | 13.7337 | 13.341 | 12.9742 | 12.6708 | 12.4358 | 12.0998 | 11.824 | 10.2681 | 7.7905 | 7.0748 | 7.643
| ELLESMERE T1 / MMB ELLESMERE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.5918 | 1.7834 | 1.6984 | 1.223 | 0.743 | 0.15436 | -0.42438 | -1.0304 | -1.6758 | -2.3091 | -2.8387 | -4.8782 | -7.519 | -8.9989 | -8.6856
| ELTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 4.7755 | 4.7155 | 4.5795 | 4.2486 | 3.8707 | 3.4397 | 3.0018 | 2.4931 | 1.9453 | 1.4145 | 0.8919 | -0.83748 | -2.8228 | -3.0755 | -2.9849
| ENGINEER PK T1 / PILKINGTONS QUEENSFERRY T1 / QUEENSFERRY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 5.6429 | 6.0843 | 6.0762 | 5.4774 | 5.0121 | 4.4228 | 3.8859 | 3.4149 | 3.0307 | 2.5468 | 2.1173 | -0.079858 | -3.356 | -4.7748 | -4.1201
| ESTUARY COMMERCE PK T1 / LEEWARD DR T1 / LEEWARD DR T2 / SPEKE HALL RD T1 / SPEKE SKY PK T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 21.1633 | 21.4255 | 21.437 | 21.1321 | 20.9118 | 20.6299 | 20.4123 | 20.2454 | 20.1557 | 20.0031 | 19.843 | 18.7959 | 17.1308 | 16.7077 | 17.0675
| EVERTON BROW T1 / GARDNERS ROW T1 / SHEIL PK T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 6.5408 | 7.7118 | 7.9633 | 8.0274 | 8.1152 | 7.9385 | 7.9134 | 7.8631 | 7.8366 | 7.7559 | 7.7264 | 7.3651 | 6.8591 | 6.8712 | 7.1573
| EXPRESS FOODS T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 5.9898 | 6.0376 | 6.0214 | 5.9444 | 5.867 | 5.7795 | 5.6832 | 5.5831 | 5.485 | 5.3759 | 5.2779 | 4.9192 | 4.4567 | 4.3811 | 4.492
| FAIRBOURNE T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 5.2755 | 5.1769 | 5.0271 | 4.628 | 4.2489 | 3.7863 | 3.324 | 2.8178 | 2.2092 | 1.6884 | 1.2605 | 0.058212 | -1.1152 | -1.2893 | -1.1988
| FAZAKERLEY HOSPITAL T1 / JACOBS T1 / JACOBS T2 / SEEDS LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 16.0306 | 17.0243 | 17.1444 | 16.8789 | 16.6324 | 16.3053 | 15.9397 | 15.5605 | 15.2162 | 14.7995 | 14.4142 | 12.7568 | 10.2659 | 9.6765 | 10.0265
| FERODO T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 4.8776 | 4.8958 | 4.7885 | 4.5239 | 4.2205 | 3.8592 | 3.4735 | 3.0546 | 2.5602 | 2.0867 | 1.662 | 0.26829 | -1.4214 | -1.6013 | -1.4516
| FISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.7347 | 4.7972 | 4.7895 | 4.65 | 4.5486 | 4.4268 | 4.3204 | 4.2184 | 4.1408 | 4.0447 | 3.9535 | 3.5264 | 2.8361 | 2.5274 | 2.5258
| FLINT T1 / FLINT T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.949 | 4.2078 | 4.2135 | -0.16327 | -0.41111 | -0.72597 | -1.0396 | -1.3526 | -1.6658 | -2.0039 | -2.3135 | -3.6041 | -5.3566 | -6.0528 | -6.3336
| FODENS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.5 | 2.5828 | 2.5208 | 2.1492 | 1.849 | 1.4748 | 1.1091 | 0.75016 | 0.40167 | 0.024213 | -0.35211 | -1.755 | -3.8688 | -4.934 | -5.2636
| FORD T1 / OXTON T1 / PRENTON LOCAL T1 / SINGLETON AVE T2 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | 12.0204 | 13.2989 | 13.0501 | 11.9446 | 10.7836 | 9.2863 | 7.6852 | 5.835 | 3.8043 | 1.7909 | 0.15601 | -5.9744 | -13.2024 | -19.9421 | -18.6284
| FORDEN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 0.29592 | 1.8416 | 1.9336 | 1.5993 | 1.4805 | 1.2684 | 0.75023 | 0.41433 | 0.035406 | -0.33355 | -0.64189 | -1.6453 | -2.9565 | -3.3019 | -3.1531
| FOUR CROSSES T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.6224 | 1.6781 | 1.6554 | 1.515 | 1.3688 | 1.2087 | 1.0475 | 0.8757 | 0.71171 | 0.53601 | 0.37411 | -0.22266 | -0.97051 | -1.166 | -1.1147
| FRODSHAM LOCAL T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 2.0476 | 2.161 | 1.9112 | 1.2809 | 0.71228 | 0.41984 | -0.76613 | -1.6505 | -2.6423 | -3.5357 | -4.344 | -7.1544 | -10.2599 | -11.4232 | -11.6374
| GADBROOK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.6735 | 3.8137 | 3.7704 | 3.5222 | 3.2573 | 2.9626 | 2.656 | 2.3068 | 1.9361 | 1.5376 | 1.1709 | -0.019425 | -1.862 | -2.4481 | -2.465
| GAERWEN VIEW T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.7653 | 5.7769 | 5.7544 | 5.6158 | 5.495 | 5.336 | 5.1889 | 5.0328 | 4.8697 | 4.6984 | 4.554 | 3.9722 | 3.219 | 3.0673 | 3.0898
| GIGG LA THELWALL T1 / HILLCLIFFE T1 / STOCKTON HEATH T1 / STRETTON IND EST T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 10.2653 | 11.2229 | 11.1441 | 10.111 | 9.0901 | 7.8133 | 6.4825 | 5.096 | 3.6947 | 2.1927 | 0.87493 | -4.1322 | -11.213 | -16.088 | -16.2552
| GILBROOK DOCK T1 / HILL RD T1 / MOBIL OIL (WALLASEY) T1 | 7 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 9.4959 | 10.1533 | 10.211 | 11.7056 | 11.4129 | 11.0367 | 10.6401 | 10.1778 | 9.7531 | 9.3116 | 8.9396 | 7.4088 | 5.7857 | 5.6368 | 5.4678
| GLAN-YR-AFON T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.1735 | 5.2498 | 5.2289 | 5.0787 | 4.9379 | 4.7646 | 4.5959 | 4.4225 | 4.248 | 4.0767 | 3.9375 | 3.4415 | 2.844 | 2.6215 | 2.6571
| GRAIG FAWR T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.2041 | 4.1501 | 3.9381 | 3.3395 | 2.622 | 1.8264 | 0.99785 | 0.096651 | -0.93609 | -1.9336 | -2.827 | -5.6684 | -9.0602 | -9.696 | -9.2728
| GRAVEL T1 / WCB PLASTICS T1 / WHARTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 13.4694 | 13.6663 | 13.6488 | 13.3911 | 13.1401 | 12.8409 | 12.5685 | 12.2809 | 12.0267 | 11.705 | 11.4167 | 10.1403 | 8.2632 | 8.0543 | 8.4474
| GREASBY T1 / SAUGHALL MASSIE T1 / UPTON T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 7.2347 | 7.8035 | 7.666 | 6.8521 | 5.9867 | 4.9214 | 3.7985 | 2.5822 | 1.3212 | 0.044291 | -1.0523 | -5.3759 | -10.775 | -14.5936 | -14.2557
| GREAT SANKEY T1 / PENKETH T1 / WIDNES RD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 9.1837 | 9.4429 | 9.2484 | 8.344 | 7.3636 | 6.187 | 4.9771 | 3.6893 | 2.3533 | 0.99925 | -0.201 | -4.8057 | -10.8394 | -14.9556 | -15.0025
| GREAT SUTTON T1 / LITTLE SUTTON T1 / STRAWBERRY ROUNDABOUT T1 / SUTTON HALL WWB T1 / WHITBY MAIN T2 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 3.42 | 4.7998 | 4.6901 | 3.4785 | 2.1744 | 0.50446 | -1.3018 | -3.2993 | -5.3767 | -7.4856 | -9.3285 | -16.4058 | -25.4427 | -31.5993 | -31.6613
| GREENFIELD T1 / GREENFIELD T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.949 | 4.0461 | 3.9444 | 3.5357 | 3.0881 | 2.5695 | 2.0326 | 1.4676 | 0.86392 | 0.22135 | -0.36888 | -2.5948 | -5.4596 | -5.6704 | -5.2528
| GROSVENOR ST T1 / LINENHALL ST T1 / NORTHGATE TERRACE T1 / STATION VIEW T1 / TOMULAR PLACE T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 8.1429 | 9.5419 | 9.6693 | 9.0377 | 8.6287 | 7.9713 | 7.3364 | 6.7203 | 6.037 | 5.3771 | 4.9367 | 3.0964 | 0.73774 | 0.051508 | 0.74034
| GWERSYLLT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.102 | 2.1442 | 1.9867 | 1.9798 | 1.8001 | 2.9869 | -0.58872 | -1.404 | -2.2955 | -3.1813 | -3.9704 | -6.7002 | -9.7496 | -10.0059 | -9.8938
| HALTON RD T1 / MURDISHAW T1 / PERCIVAL LA T4 / RUNCORN CENTRAL T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 6.4796 | 8.2535 | 8.5174 | 8.2946 | 8.1025 | 7.7952 | 7.3402 | 6.8442 | 6.3096 | 5.7094 | 5.2084 | 3.2693 | 0.22355 | -1.4589 | -1.7033
| HARLECH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.1939 | 5.1275 | 5.0106 | 4.6337 | 4.3055 | 3.8902 | 3.4589 | 2.9841 | 2.4415 | 1.9721 | 1.6056 | 0.49236 | -0.6025 | -0.92582 | -0.98303
| HARRINGTON ST T1 / PARADISE ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 3.4041 | 3.6252 | 3.3165 | 3.0136 | 3.0456 | 2.9511 | 2.7818 | 2.5183 | 2.1993 | 1.9496 | 1.6355 | 0.22884 | -1.6426 | -3.3111 | -3.5731
| HARRINGTON ST T2 / HIGHFIELD ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.4653 | 4.5916 | 4.6036 | 4.4684 | 4.3878 | 4.2827 | 4.2094 | 4.157 | 4.1434 | 4.0969 | 4.0429 | 3.6521 | 2.9757 | 2.7839 | 2.9752
| HARRINGTON ST T3 / LIME ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.4653 | 4.9486 | 5.0478 | 5.1188 | 5.1227 | 5.1817 | 5.2178 | 5.2499 | 5.2825 | 5.2947 | 5.3262 | 5.3286 | 5.28 | 5.3131 | 5.4895
| HARTFORD T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 1.2449 | 1.6474 | 1.6033 | 1.889 | 2.1322 | 0.84289 | -0.79058 | -1.5764 | -2.4374 | -3.2535 | -3.9292 | -6.2066 | -8.8339 | -10.4137 | -10.9518
| HASKAYNE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 5.3776 | 5.4692 | 5.4471 | 5.3013 | 5.1399 | 4.9439 | 4.7433 | 4.5128 | 4.2582 | 4.023 | 3.8035 | 3.0305 | 2.1459 | 2.0581 | 2.0373
| HATHERTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.8265 | 1.8516 | 1.8222 | 1.7088 | 1.6094 | 1.4865 | 1.3763 | 1.2655 | 1.156 | 1.0389 | 0.92435 | 0.50261 | -0.17381 | -0.34822 | -0.20649
| HERONS WAY T1 / LACHE T1 / MBNA T1 / SMFS KINGSMEADOW T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 19.2041 | 19.6553 | 19.6104 | 19.0386 | 18.4647 | 17.7325 | 16.9965 | 16.2224 | 15.4497 | 14.6373 | 13.936 | 11.1372 | 7.5873 | 5.4071 | 5.7565
| HIGHFIELD ST T2 / LIME ST T2 / OLD HAYMARKET T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 10.7505 | 11.0011 | 10.9779 | 10.7549 | 10.6073 | 10.4178 | 10.234 | 10.0493 | 9.8576 | 9.6585 | 9.4217 | 8.4518 | 6.8998 | 6.5903 | 6.9693
| HOLMES CHAPEL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.6939 | 1.7961 | 1.7176 | 1.3085 | 0.89914 | 0.69936 | -0.067808 | -0.55557 | -1.0816 | -1.5933 | -2.0217 | -3.5873 | -5.7194 | -6.9501 | -6.9362
| HOLT LA (WARRINGTON RD) T1 / PRESCOT T1 / RAINHILL LOCAL T1 / WHISTON HOSP T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 10.1735 | 11.6774 | 11.7317 | 11.12 | 10.4547 | 9.5119 | 8.461 | 7.2506 | 5.9697 | 4.6026 | 3.4439 | -1.1 | -6.3351 | -9.7711 | -8.7089
| HOLWAY RD T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.2143 | 3.3271 | 3.2769 | 2.9568 | 2.6647 | 2.3021 | 1.951 | 1.5902 | 1.2141 | 0.85341 | 0.57744 | -0.50949 | -1.7409 | -2.3499 | -2.3092
| HOLYHEAD T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 4.8061 | 4.8366 | 4.7585 | 4.5343 | 4.2481 | 3.9395 | 3.6131 | 3.2331 | 2.7852 | 2.3611 | 1.9589 | 0.82608 | -0.8773 | -1.1117 | -0.87576
| HOLYWELL T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.3469 | 3.4052 | 3.3008 | 2.888 | 2.4091 | 1.8704 | 1.3014 | 0.65661 | -0.0096952 | -0.66275 | -1.2273 | -3.1466 | -5.5266 | -6.2292 | -6.3052
| HOOTON MAIN T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 2.8878 | 2.8793 | 2.7622 | 2.2713 | 1.7665 | 1.1822 | 0.5825 | -0.072616 | -0.71853 | -1.3464 | -1.9209 | -4.1054 | -6.7153 | -7.7836 | -8.0498
| HUNTS CROSS T1 / KENTON RD T1 / WOODEND AVE T1 / WOOLTON T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 13.0102 | 13.8284 | 13.6495 | 12.6132 | 11.5036 | 10.1012 | 8.6259 | 7.0184 | 5.3413 | 3.6203 | 2.126 | -3.7644 | -11.3166 | -16.9679 | -16.2835
| HUYTON HEY RD T1 / WILSON RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 2.9694 | 3.2672 | 3.2205 | 2.7804 | 2.3231 | 1.7454 | 1.1695 | 0.55642 | -0.085735 | -0.7228 | -1.2568 | -3.3402 | -5.9086 | -7.5078 | -7.4282
| IFTON T1 / IFTON T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.9592 | 4.1082 | 4.0378 | 3.6025 | 3.1433 | 2.6007 | 2.0421 | 1.4412 | 0.82389 | 0.20747 | -0.34061 | -2.4522 | -5.1165 | -6.4712 | -6.352
| ILFORDS T1 / KNUTSFORD T1 / MOBBERLEY T1 / RADBROKE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 15.2857 | 15.7468 | 15.6449 | 14.9656 | 14.2285 | 13.3849 | 12.5377 | 11.6132 | 10.6889 | 9.6846 | 8.7531 | 5.2651 | 0.43448 | -0.36598 | 0.22173
| IVY ST (SOUTHPORT) T1 / KENSINGTON RD T1 / MARKET ST T1 / SOUTHPORT T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 14.6633 | 15.2202 | 15.2078 | 14.565 | 13.9364 | 13.2025 | 12.5086 | 11.8063 | 11.1261 | 10.3777 | 9.7097 | 7.032 | 3.1392 | 2.2673 | 2.7482
| IVY ST T1 / LLYSFAEN RD T1 / OLD MILL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 7.9184 | 8.6394 | 8.5328 | 7.7545 | 6.9483 | 5.9013 | 4.8128 | 3.6041 | 2.2723 | 1.0111 | 0.029116 | -3.5215 | -7.4663 | -10.3461 | -10.072
| JOHNSTOWN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.0816 | 1.0993 | 0.92752 | 0.73593 | 0.07496 | -0.54017 | -1.6002 | -2.377 | -3.2223 | -4.0785 | -4.8679 | -7.6101 | -10.9194 | -10.6831 | -10.0828
| KELCO T1 / NEWS INTERNATIONAL T1 / NEWS INTERNATIONAL T2 / PALCO T1 / SOUTHDENE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 12.4286 | 13.0134 | 13.0708 | 22.4884 | 22.0966 | 21.5937 | 21.1738 | 20.8695 | 20.7081 | 20.4031 | 20.1001 | 18.1087 | 14.8867 | 13.8972 | 14.5231
| KINGSLAND 33 T1 / SAFEWAY T1 / WOOLSTON T1 / WOOLSTON T2 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 12.7857 | 14.1303 | 14.301 | 13.96 | 13.6343 | 13.1573 | 12.6145 | 12.0469 | 11.483 | 10.8482 | 10.3048 | 6.5745 | 1.8479 | 1.87 | 2.813
| KINNERTON T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 4.1939 | 4.1197 | 3.9927 | 3.6635 | 3.2476 | 2.818 | 2.3704 | 1.857 | 1.2943 | 0.73849 | 0.20257 | -1.2997 | -3.4215 | -3.8836 | -3.5434
| KIRKBY CENTRAL T1 / NORTHWOOD T1 / TOWER HILL (BANK LA) T1 / WESTVALE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 11.7857 | 13.2484 | 13.2366 | 12.6289 | 11.8892 | 10.8377 | 9.6878 | 8.3785 | 6.9445 | 5.5132 | 4.3427 | -0.39506 | -5.9718 | -10.7183 | -9.2762
| KNOWSLEY T1 / MARLED HEY T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 5.6531 | 5.8885 | 5.9023 | 5.7065 | 5.5426 | 5.3366 | 5.1127 | 4.8835 | 4.6671 | 4.4333 | 4.21 | 3.3322 | 2.1418 | 1.6912 | 1.5387
| KNUTSFORD T2 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.9417 | 2.124 | 2.078 | 1.8076 | 1.5179 | 1.1807 | 0.84313 | 0.42114 | 0.045577 | -0.33876 | -0.6842 | -1.9375 | -3.5891 | -4.113 | -4.049
| LCWW HUNTINGTON T1 / LCWW HUNTINGTON T2 | 7 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.549 | 4.7064 | 4.6952 | 4.4947 | 4.3209 | 4.0973 | 3.8876 | 3.6742 | 3.4677 | 3.2496 | 3.0527 | 2.1881 | 0.91572 | 0.2554 | 0.46684
| LEA GREEN T1 / PILKINGTONS HO T1 / RAVENHEAD RETAIL PK T1 / SOMERFIELD DISTRIBUTION T1 | 11 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 7.1327 | 8.1623 | 8.2944 | 8.012 | 7.7663 | 7.4062 | 7.0023 | 6.5736 | 6.1521 | 5.6524 | 5.2233 | 3.511 | 0.86946 | -0.38889 | -0.62467
| LEGACY LOCAL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.2041 | 5.4018 | 5.401 | 5.3041 | 5.1585 | 4.9699 | 4.756 | 4.4994 | 4.2226 | 3.9629 | 3.7372 | 3.0199 | 2.3777 | 2.3924 | 2.4455
| LEIGHTON HOSP T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.9796 | 4.2742 | 4.2948 | 4.2551 | 4.1751 | 4.0965 | 3.9866 | 3.8464 | 3.6976 | 3.5643 | 3.4655 | 2.913 | 1.9983 | 1.9159 | 2.2283
| LIVERPOOL RD 33 T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 6.9592 | 7.1109 | 7.041 | 6.7472 | 6.4374 | 6.0445 | 5.6527 | 5.2198 | 4.7204 | 4.2511 | 3.8739 | 2.5711 | 1.2079 | 1.3261 | 1.6187
| LLAINGOCH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 4.3061 | 4.4235 | 4.2558 | 3.8948 | 3.406 | 2.8126 | 2.179 | 1.4329 | 0.53272 | -0.33467 | -1.0943 | -3.3103 | -5.566 | -5.1762 | -4.6063
| LLANARMON T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 5.9286 | 5.9924 | 5.9777 | 5.8978 | 5.7964 | 5.6869 | 5.564 | 5.4371 | 5.3066 | 5.1709 | 5.0573 | 4.6446 | 4.0093 | 3.5959 | 3.5728
| LLANBEDROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.9694 | 1.9731 | 1.9097 | 1.6592 | 1.3948 | 1.0787 | 0.77928 | 0.43718 | 0.047111 | -0.29365 | -0.57243 | -1.3894 | -2.1758 | -2.2183 | -2.1963
| LLANBERIS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 1.4592 | 1.5969 | 1.5601 | 1.3019 | 1.0456 | 0.71361 | 0.39187 | 0.040915 | -0.35943 | -0.73544 | -1.0137 | -1.9272 | -2.8554 | -2.8818 | -2.6774
| LLANDDEUSANT T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.7653 | 3.8774 | 3.7941 | 3.5304 | 3.2008 | 2.8369 | 2.4349 | 1.9679 | 1.431 | 0.91365 | 0.45224 | -0.90402 | -2.4406 | -2.6834 | -2.315
| LLANDDU QUARRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 0.52041 | 0.69751 | 0.70447 | 0.56024 | 0.41437 | 0.23592 | 0.051503 | -0.14483 | -0.33794 | -0.53761 | -0.7249 | -1.4359 | -2.4314 | -2.901 | -2.8524
| LLANDEGFAN T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.0204 | 5.1065 | 5.0737 | 4.9141 | 4.7121 | 4.4855 | 4.2356 | 3.9547 | 3.6545 | 3.3689 | 3.1145 | 2.1975 | 0.95407 | 0.10406 | 0.16779
| LLANDRINIO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.5353 | 2.5496 | 2.4931 | 2.4125 | 2.3248 | 2.0628 | 1.4954 | 1.2056 | 0.90242 | 0.60556 | 0.33896 | -0.62359 | -1.9631 | -2.4635 | -2.4889
| LLANDUDNO T1 / LLANDUDNO T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.8878 | 4.2896 | 4.266 | 4.0092 | 3.7033 | 3.3406 | 2.9535 | 2.5086 | 1.9766 | 1.4622 | 1.0428 | -0.12705 | -1.8434 | -2.2695 | -2.0268
| LLANDYFRYDOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.1531 | 5.2052 | 5.1601 | 4.9381 | 4.7199 | 4.44 | 4.1634 | 3.8769 | 3.5399 | 3.2449 | 3.0014 | 2.2426 | 1.2985 | 0.76457 | 0.7131
| LLANDYRNOG T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 1.9184 | 2.0786 | 2.0768 | 1.9528 | 1.8237 | 1.6687 | 1.5006 | 1.3313 | 1.1554 | 0.9694 | 0.81701 | 0.20731 | -0.7181 | -1.2561 | -1.1813
| LLANFAELOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 1.2857 | 1.3553 | 1.3318 | 1.1978 | 1.0609 | 0.89085 | 0.72188 | 0.55379 | 0.37814 | 0.20413 | 0.062721 | -0.46681 | -1.1198 | -1.143 | -0.80796
| LLANFAIR CAEREINION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.4388 | 2.539 | 2.4178 | 1.996 | 1.5164 | 0.97591 | 0.41737 | -0.20657 | -0.89775 | -1.5467 | -2.0843 | -3.7624 | -5.6874 | -6.2042 | -5.9999
| LLANFAIR PG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.3571 | 3.4995 | 3.4128 | 3.0821 | 2.7009 | 2.2446 | 1.7696 | 1.2348 | 0.59951 | -0.00039513 | -0.50036 | -1.979 | -3.255 | -3.154 | -2.7629
| LLANFAIRFECHAN T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 5.4082 | 5.4359 | 5.3761 | 5.1211 | 4.8611 | 4.5302 | 4.222 | 3.8849 | 3.471 | 3.1126 | 2.8469 | 2.0082 | 1.2436 | 0.74037 | 0.8075
| LLANFROTHEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.4082 | 5.3748 | 5.2937 | 4.983 | 4.6445 | 4.2543 | 3.8641 | 3.43 | 2.9435 | 2.5086 | 2.1537 | 0.99691 | -0.18311 | -0.23634 | -0.26641
| LLANFWROG T1 / RUTHIN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 5.7959 | 6.2057 | 6.1404 | 5.6203 | 5.0562 | 4.3797 | 3.672 | 2.9134 | 1.8985 | 1.0793 | 0.13811 | -3.1119 | -7.2152 | -7.4563 | -7.0457
| LLANFYLLIN T1 / LLANFYLLIN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.5449 | 2.7899 | 4.9406 | 4.4972 | 4.0596 | 3.4994 | 2.9394 | 2.3393 | 1.6199 | 0.99457 | 0.56489 | -0.82288 | -2.1774 | -2.8934 | -2.9747
| LLANGAFFO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.8061 | 3.8838 | 3.8441 | 3.62 | 3.3843 | 3.0873 | 2.7997 | 2.4744 | 2.1555 | 1.8198 | 1.5247 | 0.39466 | -1.1771 | -2.1465 | -1.9803
| LLANGEFNI IND EST T1 / LLANGEFNI IND EST T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5204 | 3.7304 | 3.7426 | 3.5281 | 3.3645 | 3.1633 | 2.9801 | 2.8347 | 2.741 | 2.5896 | 2.4409 | 1.6093 | 0.26814 | -0.15208 | 0.12672
| LLANGEFNI T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5612 | 3.6588 | 3.6039 | 3.2994 | 2.9884 | 2.6009 | 2.2107 | 1.7974 | 1.3634 | 0.9289 | 0.56452 | -0.80936 | -2.3244 | -2.6237 | -2.5722
| LLANGOLLEN T1 / LLANGOLLEN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.0918 | 5.2705 | 5.2189 | 4.8456 | 4.4551 | 3.9704 | 3.477 | 2.9529 | 2.3551 | 1.804 | 1.406 | 0.034219 | -1.4702 | -2.3859 | -2.163
| LLANIDLOES T1 / LLANIDLOES T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.3729 | 1.5099 | 1.3895 | 0.81539 | 0.49078 | 0.099735 | -1.2418 | -2.0356 | -3.0609 | -3.9298 | -4.5482 | -6.3167 | -7.8708 | -7.7971 | -7.9925
| LLANILAR T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 0.78163 | 0.79526 | 0.72993 | 0.50376 | 0.52764 | 0.60092 | -0.38805 | -0.73758 | -1.1141 | -1.48 | -1.8027 | -2.8126 | -3.9781 | -4.2441 | -4.1522
| LLANRWST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.9592 | 4.1514 | 4.1244 | 3.8808 | 3.629 | 3.3042 | 2.9717 | 2.6054 | 2.1816 | 1.8054 | 1.5309 | 0.61493 | -0.28919 | -0.82798 | -0.62737
| LLANSANNAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.7449 | 4.7652 | 4.6874 | 4.3878 | 4.0602 | 3.6828 | 3.2969 | 2.8837 | 2.3853 | 1.9573 | 1.6351 | 0.8246 | -0.0089489 | -0.1831 | 0.0086211
| LLANSILIN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.9898 | 4.079 | 4.0005 | 3.6931 | 3.3331 | 2.9192 | 2.5003 | 2.0333 | 1.4966 | 1.0106 | 0.60859 | -0.51387 | -1.7837 | -2.1356 | -2.0105
| LLYNCLYS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.3265 | 3.2743 | 3.148 | 2.7846 | 2.3294 | 1.847 | 1.3664 | 0.81259 | 0.21617 | -0.37455 | -0.92826 | -2.494 | -4.8294 | -5.377 | -5.0731
| LORD ST T1 / MARSHSIDE T1 / MULLARDS BALMORAL DV T1 / SOUTHPORT T2 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 11.949 | 13.0816 | 12.7752 | 11.282 | 9.4844 | 7.2756 | 4.8902 | 2.1342 | -0.81218 | -3.6641 | -6.0974 | -15.0044 | -25.1868 | -32.3126 | -32.4963
| LOSTOCK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.1531 | 3.2531 | 3.1599 | 2.8325 | 2.4486 | 2.0187 | 1.5519 | 1.0502 | 0.50457 | -0.043676 | -0.54078 | -2.2989 | -4.6302 | -5.4385 | -5.3712
| LOSTOCK TRIANGLE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.6327 | 4.6082 | 4.5319 | 4.3752 | 4.1352 | 3.8956 | 3.6681 | 3.3804 | 3.0679 | 2.7248 | 2.3956 | 1.3993 | -0.32277 | -0.722 | -0.43269
| LOWER BEBINGTON T1 / NEW FERRY T1 / SPITAL T1 / UNILEVER RESEARCH T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 15.2245 | 15.578 | 15.1898 | 13.8557 | 12.4759 | 10.7739 | 8.9894 | 7.0039 | 4.8627 | 2.7585 | 0.91861 | -5.8348 | -13.37 | -18.0547 | -17.5643
| LUGSDALE T1 / PILK SULLIVAN T1 / PILK SULLIVAN T2 / USAC T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 20.398 | 20.7082 | 20.7265 | 20.3428 | 20.1276 | 19.8324 | 19.5837 | 19.4223 | 19.3414 | 19.1968 | 19.062 | 18.0888 | 16.5826 | 16.3732 | 16.9064
| LYMM T1 / WHITELEGGS LA T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 0.94898 | 2.7775 | 2.6139 | 2.5366 | 1.0844 | 0.38418 | -0.97863 | -2.183 | -3.5291 | -4.8628 | -6.0591 | -9.9245 | -14.5589 | -14.6521 | -14.307
| MACHYNLLETH T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 1.4082 | 1.4051 | 1.3011 | 0.97099 | 0.60457 | 0.16304 | -0.28939 | -0.80448 | -1.4345 | -1.9901 | -2.4282 | -3.7829 | -5.0855 | -4.6963 | -4.328
| MACHYNLLETH T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.3773 | 2.385 | 2.3138 | 2.0402 | 1.7459 | 1.3952 | 1.0445 | 0.6555 | 0.20301 | -0.20378 | -0.53035 | -1.5084 | -2.5129 | -2.6476 | -2.5482
| MAELOR CREAMERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.0612 | 4.22 | 4.2276 | 4.1165 | 4.0279 | 3.9283 | 3.8225 | 3.7418 | 3.6648 | 3.5662 | 3.4836 | 3.0745 | 2.4513 | 2.2973 | 2.4667
| MAENTWROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.9082 | 5.8864 | 5.8215 | 5.6247 | 5.4343 | 5.2039 | 4.9586 | 4.7019 | 4.4183 | 4.1564 | 3.9286 | 3.148 | 2.3173 | 2.218 | 2.1803
| MAES-Y-CLAWDD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.8163 | 2.966 | 2.9386 | 2.7159 | 2.4877 | 2.2458 | 2.0123 | 1.5743 | 1.1152 | 0.60698 | 0.071728 | -1.7207 | -4.3813 | -5.0384 | -4.8671
| MANOD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.8571 | 2.806 | 2.7449 | 2.5509 | 2.3519 | 2.1066 | 1.8659 | 1.605 | 1.2955 | 1.0176 | 0.79668 | 0.24017 | -0.36102 | -0.31846 | -0.20409
| MANOR PK T1 / NORTON CHAINS T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 0.84694 | 2.2613 | 1.7145 | 0.85592 | 0.46004 | 0.019104 | -0.54956 | -1.2445 | -2.0393 | -2.6413 | -3.4155 | -6.8693 | -11.5204 | -14.9565 | -15.6045
| MDHB EGERTON DOCK T1 / MDHB EGERTON DOCK T2 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 3.5485 | 3.9529 | 3.8463 | 3.2748 | 3.5325 | 2.7952 | 2.0398 | 1.173 | 0.2495 | -0.69118 | -1.5229 | -4.6176 | -8.6538 | -10.9099 | -10.4576
| MERE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.7653 | 2.739 | 2.5565 | 1.9574 | 2.1247 | 2.6859 | -0.31938 | -1.2186 | -2.1818 | -3.1046 | -3.9009 | -6.6686 | -9.7826 | -10.4533 | -10.9009
| MERES EDGE T1 / MERES EDGE T2 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 5.4694 | 5.496 | 5.3421 | 4.8738 | 4.3145 | 3.6676 | 3.0078 | 2.2609 | 1.3994 | 0.58196 | -0.13925 | -2.4764 | -5.1953 | -5.5807 | -5.4371
| MIDDLEWICH T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.7653 | 3.7444 | 3.7998 | 5.0976 | 4.5143 | 4.05 | 3.5996 | 2.4354 | 1.9132 | 1.4123 | 0.98624 | -0.60121 | -2.4267 | -3.334 | -3.266
| MIDPOINT POCHIN WAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 5.7755 | 5.8271 | 5.8198 | 5.7591 | 5.7153 | 5.6554 | 5.6008 | 5.5568 | 5.5262 | 5.4775 | 5.4344 | 5.2036 | 4.8091 | 4.6803 | 4.7415
| MILFORD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.9388 | 3.1109 | 3.0563 | 2.7611 | 2.4508 | 2.0771 | 1.7217 | 1.3021 | 0.83207 | 0.39645 | 0.016126 | -1.1817 | -2.7972 | -3.1355 | -3.045
| MINFFORDD T1 / PARC BRYN CEGIN T1 / PARC BRYN CEGIN T2 | 11 | BANGOR GT2 / CAERNARFON GT2 | 16.3265 | 16.4272 | 16.3714 | 16.1118 | 15.8373 | 15.479 | 15.1153 | 14.7495 | 14.3265 | 13.9223 | 13.594 | 12.316 | 10.9662 | 10.201 | 10.6465
| MOCHDRE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.7857 | 3.9192 | 3.9121 | 3.7598 | 3.6316 | 3.4729 | 3.329 | 3.2005 | 3.0789 | 2.934 | 2.8073 | 2.2119 | 1.3998 | 1.1667 | 1.1813
| MONA T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.7347 | 5.7474 | 5.7149 | 5.5689 | 5.4141 | 5.2315 | 5.0401 | 4.8401 | 4.6256 | 4.4054 | 4.2269 | 3.5383 | 2.6405 | 2.3069 | 2.2666
| MONSANTO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.9898 | 5.9721 | 5.8934 | 5.6381 | 5.3869 | 5.0661 | 4.76 | 4.415 | 3.9946 | 3.643 | 3.3673 | 2.4646 | 1.6199 | 1.2007 | 1.0921
| MORDA T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 4.102 | 4.0768 | 3.9461 | 3.6105 | 3.1497 | 2.6493 | 2.1226 | 1.5064 | 0.83057 | 0.14667 | -0.49752 | -2.4734 | -4.553 | -4.5787 | -4.1863
| MORGANITE CERAMICS T1 / PLYMYARD T2 / VAUXHALL NORTH RD T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 13.102 | 13.1901 | 13.0364 | 12.4282 | 11.779 | 10.9936 | 10.1934 | 9.3093 | 8.394 | 7.4519 | 6.5798 | 3.2635 | -0.70197 | -1.4811 | -1.4263
| MORRISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.0816 | 2.2375 | 2.2175 | 1.973 | 1.7515 | 1.493 | 1.2526 | 1.0072 | 0.7995 | 0.56807 | 0.33837 | -0.63258 | -1.9311 | -2.2434 | -2.1257
| NANTWICH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.8163 | 1.9205 | 1.7869 | 1.3665 | 1.5895 | 2.0977 | 0.099692 | -0.4199 | -0.98302 | -1.5339 | -2.086 | -3.8802 | -6.6346 | -7.7479 | -7.7862
| NANT-Y-GAMAR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 2.6531 | 2.8058 | 2.7511 | 2.4036 | 2.0555 | 1.7427 | 1.2137 | 0.78055 | 0.32906 | -0.1188 | -0.51188 | -2.0095 | -3.9222 | -5.051 | -5.0538
| NEVILL ST T1 / OCEAN PLAZA T1 / YORK RD T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 9.551 | 9.8522 | 9.8542 | 9.3879 | 9.0373 | 8.5836 | 8.1941 | 7.8561 | 7.5773 | 7.249 | 6.9688 | 5.543 | 3.4988 | 2.8874 | 3.1496
| NEW BRIGHTON T1 / SEAVIEW RD T2 / WALLASEY T1 / WALLASEY VILLAGE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 15.449 | 16.6247 | 16.6192 | 15.7944 | 14.9738 | 13.9188 | 12.7891 | 11.5246 | 10.0829 | 8.7341 | 7.7128 | 4.5741 | 0.89127 | -1.0162 | -2.2225
| NEWHALL T1 / NEWHALL T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 6 | 6.1099 | 6.1081 | 5.9419 | 5.8132 | 5.6635 | 5.5139 | 5.3821 | 5.2731 | 5.1359 | 5.0104 | 4.3832 | 3.4164 | 3.1091 | 3.2731
| NORTH WALES PAPER T1 / NORTH WALES PAPER T2 / WOODFIELD AVE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 7.398 | 7.8353 | 7.8084 | 7.2842 | 6.8475 | 6.292 | 5.7668 | 5.277 | 4.8425 | 4.3249 | 3.8764 | 1.7028 | -1.4503 | -3.2309 | -2.5723
| NORTH WEST WATER CAMPUS T1 / NORTH WEST WATER CAMPUS T2 / OMEGA T1 / OMEGA T2 / ORION BOULEVARD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 24.8776 | 25.8151 | 25.9286 | 25.5969 | 25.3581 | 25.0204 | 24.6744 | 24.1664 | 23.9043 | 23.5508 | 23.2583 | 21.7783 | 19.7665 | 19.5786 | 20.3852
| OPTICAL FIBRES T1 / SHOTWICK T1 / WALBRO T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 7.2041 | 7.5749 | 7.6106 | 7.1862 | 6.9081 | 6.5655 | 6.2893 | 6.121 | 6.0688 | 5.8942 | 5.726 | 4.4297 | 2.1841 | 1.5926 | 2.2287
| ORB CL T1 / STONEBRIDGE LA T1 / STONEBRIDGE LA T2 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 10.8163 | 11.1139 | 11.1099 | 10.7114 | 10.3979 | 10.0024 | 9.638 | 9.3072 | 9.0369 | 8.7041 | 8.3926 | 6.8645 | 4.5629 | 3.7282 | 3.7734
| ORFORD T1 / PADGATE T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 1.051 | 4.8144 | 4.6841 | 2.4431 | 1.2417 | -0.34638 | -2.1365 | -4.2834 | -6.7848 | -9.0396 | -11.2031 | -19.1524 | -28.0754 | -35.7664 | -35.6642
| OTIS ELEVATOR T1 / ST IVEL FOODS T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 5.0306 | 5.1721 | 5.1895 | 5.0198 | 4.9123 | 4.7789 | 4.6699 | 4.5992 | 4.5803 | 4.5136 | 4.4471 | 3.9353 | 3.0862 | 2.8806 | 3.1437
| OVERTON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.8571 | 3.8593 | 3.7382 | 3.1674 | 2.6607 | 2.0051 | 1.3935 | 0.74037 | -0.080392 | -0.74086 | -1.1195 | -2.0209 | -2.3955 | -2.2771 | -2.2435
| PANDY T1 / PANDY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 1.7143 | 2.3587 | 2.3953 | 2.0748 | 1.7584 | 1.3356 | 0.8641 | 0.32734 | -0.26087 | -0.84454 | -1.3919 | -3.3162 | -5.9638 | -7.1337 | -7.7197
| PARC CYBI T1 / PARC CYBI T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 7.0816 | 7.108 | 7.0538 | 6.8172 | 6.5872 | 6.3222 | 6.072 | 5.8142 | 5.5295 | 5.2766 | 5.0573 | 4.3097 | 3.3472 | 3.0594 | 3.058
| PARC MENAI T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 5.9898 | 5.9998 | 5.9537 | 5.8405 | 5.7037 | 5.548 | 5.3779 | 5.2007 | 4.9889 | 4.778 | 4.5725 | 3.9979 | 3.2203 | 3.1735 | 3.3702
| PEBLIC MILLS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 6.398 | 6.356 | 6.3011 | 6.1705 | 5.8838 | 5.6941 | 5.4992 | 5.0946 | 4.5975 | 4.0855 | 3.5914 | 2.2796 | 0.36165 | -0.10574 | 0.13239
| PENMAENMAWR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 5.1429 | 5.1374 | 5.0346 | 4.6674 | 4.2887 | 3.824 | 3.3648 | 2.8438 | 2.2144 | 1.6645 | 1.2198 | -0.12288 | -1.4466 | -1.3679 | -1.2781
| PENTRAETH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.0612 | 3.1907 | 3.1394 | 2.7643 | 2.4093 | 1.962 | 1.5374 | 1.0706 | 0.57846 | 0.12211 | -0.23482 | -1.5123 | -3.0564 | -3.87 | -4.0896
| PEN-Y-GROES T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 2.3122 | 2.3007 | 2.2235 | 1.8931 | 1.5482 | 1.139 | 0.73486 | 0.31386 | -0.18145 | -0.6246 | -0.95127 | -2.0363 | -3.5427 | -4.2332 | -4.0977
| PILKINGTONS T1 / PILKINGTONS T2 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 6.4592 | 6.6158 | 6.6169 | 6.4647 | 6.3261 | 6.1457 | 5.9594 | 5.777 | 5.5988 | 5.3974 | 5.2523 | 4.6415 | 3.7698 | 3.2906 | 3.4281
| POINT OF AYR COLLIERY T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 2.2755 | 2.3799 | 2.3202 | 2.0064 | 1.6728 | 1.2787 | 0.8944 | 0.51008 | 0.076523 | -0.34807 | -0.71547 | -2.0163 | -3.6288 | -3.8724 | -3.5674
| PORTHMADOG T1 / PORTHMADOG T2 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.6633 | 5.7504 | 5.6373 | 5.1904 | 4.6986 | 4.0936 | 3.4852 | 2.8139 | 2.0172 | 1.2988 | 0.73756 | -1.0124 | -2.8466 | -2.5663 | -2.3372
| PREES T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 2.1633 | 2.5128 | 2.5035 | 2.3064 | 2.04 | 1.7325 | 1.3753 | 0.98269 | 0.51863 | 0.090588 | -0.28929 | -1.3954 | -2.7481 | -3.01 | -2.7271
| PRIMROSE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.8265 | 4.8937 | 4.8823 | 4.7361 | 4.6048 | 4.4457 | 4.3015 | 4.1552 | 4.0184 | 3.8772 | 3.7379 | 3.1827 | 2.433 | 2.2022 | 2.1733
| PWLLHELI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.8673 | 4.0295 | 3.9954 | 3.7345 | 3.4737 | 3.1349 | 2.7978 | 2.4387 | 2.0384 | 1.6713 | 1.4014 | 0.44895 | -0.46288 | -1.0347 | -0.91243
| RADWAY GREEN T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.3469 | 1.5352 | 1.4754 | 1.0728 | 1.3414 | 1.5869 | -0.26602 | -0.75672 | -1.2417 | -1.7422 | -2.1811 | -3.872 | -6.1368 | -7.5535 | -7.6336
| RAVEN SQUARE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.0102 | 1.2409 | 1.1853 | 0.77853 | 0.39025 | 0.44932 | -0.60527 | -1.1274 | -1.708 | -2.2619 | -2.7494 | -4.5619 | -6.5183 | -6.6931 | -6.5687
| REFORM ST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 2.7551 | 3.0084 | 2.9608 | 2.6967 | 2.5122 | 2.2578 | 2.0011 | 1.7096 | 1.3542 | 1.0324 | 0.79028 | 0.033019 | -0.90688 | -1.3478 | -1.2063
| RHM FOODS LTD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 6.2347 | 6.2716 | 6.2738 | 6.2262 | 6.1993 | 6.1648 | 6.1383 | 6.1181 | 6.1073 | 6.092 | 6.0766 | 5.9448 | 5.7317 | 5.6721 | 5.7279
| RHOSLAN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.2143 | 4.2126 | 4.0861 | 3.6609 | 3.1593 | 2.5926 | 2.0136 | 1.3341 | 0.57327 | -0.11898 | -0.71924 | -2.4491 | -4.0631 | -4.121 | -4.0095
| RHUDDLAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.2857 | 3.5643 | 3.5242 | 3.3018 | 2.9986 | 2.6454 | 2.2563 | 1.8054 | 1.2917 | 0.79285 | 0.36694 | -0.95062 | -2.3272 | -2.3058 | -2.1652
| RHYDLYDAN T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.9286 | 2.9241 | 2.8684 | 2.7302 | 2.5342 | 2.3302 | 2.1096 | 1.8608 | 1.5622 | 1.297 | 1.0805 | 0.51053 | -0.19642 | -0.31142 | -0.24846
| RHYD-Y-FOEL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 4.9184 | 4.8447 | 4.7315 | 4.4105 | 4.0448 | 3.6303 | 3.2215 | 2.6963 | 2.1715 | 1.6874 | 1.2697 | 0.11902 | -1.225 | -1.3633 | -1.0528
| RINGWAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | -0.046939 | 6.5729 | 6.5244 | 6.3153 | 6.0249 | 5.7081 | 5.3571 | 4.9399 | 4.4828 | 4.0491 | 3.6504 | 2.5328 | 1.3751 | 1.3521 | 1.3865
| RIVALS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.6224 | 2.5546 | 2.4613 | 2.2463 | 3.1868 | 2.8991 | 2.6142 | 2.2853 | 1.8785 | 1.5326 | 1.2218 | 0.47472 | -0.33947 | -0.41432 | -0.21909
| ROLLS ROYCE T1 / ROLLS ROYCE T2 / ROLLS ROYCE T3 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.1224 | 4.0453 | 4.1504 | 3.9611 | 3.8229 | 3.6197 | 3.3806 | 2.9285 | 2.4132 | 1.852 | 1.2798 | -0.71206 | -3.8407 | -4.8538 | -4.5667
| ROSSETT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.2245 | 3.4955 | 2.5606 | 1.7408 | 0.79789 | 0.047835 | -0.89748 | -2.0888 | -3.5626 | -4.6144 | -5.9054 | -10.212 | -15.6556 | -19.1978 | -20.0551
| ROYAL INSURANCE (NEW QUAY) T1 / ROYAL INSURANCE (NEW QUAY) T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 8.2612 | 8.1596 | 8.0576 | 7.9146 | 7.7214 | 7.4994 | 7.2599 | 6.9429 | 6.5667 | 6.1928 | 5.8102 | 4.8733 | 3.2564 | 3.0462 | 3.3538
| RUABON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.1837 | 3.3884 | 3.2887 | 2.8534 | 2.4235 | 1.8799 | 1.3298 | 0.74812 | 0.14916 | -0.4548 | -0.97585 | -3.102 | -5.7637 | -7.6946 | -7.3379
| SALTNEY T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.9388 | 4.9588 | 4.9197 | 4.7642 | 4.5994 | 4.4138 | 4.2303 | 4.0305 | 3.8121 | 3.5863 | 3.3817 | 2.6521 | 1.6198 | 1.4752 | 1.7258
| SANDBACH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | -0.16327 | 1.1929 | 9.4939 | 9.9287 | 6.8251 | 6.3025 | 5.7871 | 5.2506 | 4.6923 | 4.1414 | 3.6756 | 1.8747 | -0.42674 | -1.7919 | -1.7367
| SHAWBURY T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.4601 | 1.5243 | 1.4446 | 1.096 | 0.71418 | 0.30816 | -0.099467 | -0.70453 | -1.3689 | -2.0599 | -2.7407 | -5.0207 | -7.9945 | -8.8926 | -8.6977
| SMALLWOOD T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.7653 | 1.7309 | 1.426 | 1.8887 | 1.7195 | 0.69786 | -1.307 | -2.2398 | -3.2843 | -4.2345 | -5.185 | -8.3074 | -11.954 | -13.065 | -12.8291
| SNOWHILL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.9184 | 2.0547 | 1.9583 | 1.5725 | 1.1731 | 0.70773 | 0.25986 | -0.24514 | -0.81155 | -1.3779 | -1.8757 | -3.3996 | -5.7026 | -6.4695 | -6.3611
| ST ASAPH BUSINESS PK T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 2.9997 | 2.8487 | 2.6506 | 2.2166 | 1.899 | 1.435 | 0.97076 | 0.3785 | -0.54241 | -1.3424 | -2.0008 | -4.0637 | -5.657 | -6.4632 | -4.9553
| ST HELENS RD T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 3.2245 | 3.3578 | 3.3204 | 3.0579 | 2.7989 | 2.466 | 2.1497 | 1.8146 | 1.4505 | 1.0877 | 0.80699 | -0.2886 | -1.4836 | -2.1095 | -1.7211
| STAPELEY T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4592 | 2.5021 | 2.2249 | 1.6816 | 1.3712 | 0.93874 | 0.44282 | -0.14633 | -0.8047 | -1.3383 | -1.9483 | -4.2837 | -7.2922 | -9.4997 | -9.9496
| TACO PLASTICS T1 / TACO PLASTICS T2 / UNITED PERIPHERALS T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 8.9082 | 9.155 | 9.1149 | 8.4651 | 8.1109 | 7.6125 | 7.1637 | 6.8487 | 6.59 | 6.2703 | 6.0177 | 4.7603 | 3.059 | 3.3227 | 4.2331
| TARPORLEY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.2959 | 3.4298 | 3.3601 | 3.0451 | 2.674 | 2.2487 | 1.8041 | 1.2899 | 0.74854 | 0.22462 | -0.2436 | -1.8002 | -3.7229 | -4.1279 | -4.1304
| TARVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 1.5204 | 1.7747 | 1.7215 | 1.3995 | 1.3597 | 1.8868 | -0.21384 | -0.84537 | -1.4991 | -2.1609 | -2.7351 | -4.8094 | -7.5998 | -9.2583 | -9.3192
| TRYWERYN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.2755 | 2.3485 | 2.3403 | 2.2266 | 2.1372 | 2.0122 | 1.908 | 1.7907 | 1.656 | 1.5377 | 1.4852 | 1.3078 | 1.1709 | 1.1179 | 1.2029
| TWYFORDS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.4388 | 4.609 | 4.5818 | 4.4122 | 4.2412 | 4.0202 | 3.7974 | 3.5595 | 3.3042 | 3.0416 | 2.8127 | 1.9326 | 0.73628 | -0.1725 | -0.11072
| TYWYN T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 3.2041 | 3.2283 | 3.0602 | 2.4816 | 2.0461 | 1.4087 | 0.79713 | 0.12453 | -0.68861 | -1.3862 | -1.8991 | -3.6193 | -5.2139 | -6.2736 | -6.4425
| WAENFAWR T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 4.3571 | 4.4174 | 4.3323 | 3.9834 | 3.5794 | 3.1025 | 2.6234 | 2.0663 | 1.4691 | 0.91796 | 0.44953 | -1.0857 | -2.7595 | -2.9988 | -3.0767
| WELSHPOOL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.5204 | 3.6294 | 3.5923 | 3.3747 | 3.141 | 2.8917 | 2.6151 | 2.3418 | 2.0627 | 1.7654 | 1.4971 | 0.5657 | -0.71365 | -1.1479 | -0.96057
| WEM EAST T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 4.5612 | 4.6615 | 4.6392 | 4.4532 | 4.2647 | 4.0315 | 3.8063 | 3.577 | 2.9757 | 2.6962 | 2.1748 | 0.5326 | -1.1639 | -0.59175 | -0.12939
| WEM T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 2.6939 | 2.8243 | 2.7372 | 2.4219 | 2.0184 | 1.5808 | 1.1144 | 0.56754 | -0.034279 | -0.63019 | -1.181 | -2.8928 | -5.0001 | -5.4971 | -5.1298
| WERVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.2857 | 4.291 | 4.1869 | 3.8851 | 3.5006 | 3.0854 | 2.6472 | 2.1648 | 1.5909 | 1.0412 | 0.55089 | -0.85192 | -2.888 | -3.4176 | -3.3419
| WEST FELTON T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.0204 | 1.1047 | 1.0862 | 0.93296 | 0.76476 | 0.58177 | 0.38649 | 0.18934 | -0.01921 | -0.23212 | -0.43252 | -1.113 | -2.0311 | -2.2888 | -2.081
| WESTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.8673 | 3.1208 | 3.0254 | 2.5854 | 2.1076 | 1.5454 | 0.94636 | 0.29662 | -0.39211 | -1.0727 | -1.6846 | -3.9496 | -7.0321 | -8.9715 | -8.8137
| WHEELOCK T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4286 | 2.644 | 2.5833 | 2.2223 | 1.8111 | 1.3282 | 0.80764 | 0.22598 | -0.40855 | -1.0254 | -1.5659 | -3.532 | -5.9487 | -7.3314 | -7.4103
| WHITCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 5.8571 | 6.1064 | 6.0872 | 5.808 | 5.504 | 5.1406 | 4.7417 | 4.3237 | 3.8841 | 3.4504 | 3.0718 | 1.6602 | -0.24605 | -1.2696 | -1.2598
| WIMPEYS PANT QUARRY T1 / WIMPEYS PANT QUARRY T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 1.0673 | 6.093 | 6.0655 | 5.8716 | 5.6339 | 5.3735 | 5.0831 | 4.7655 | 4.4365 | 4.0987 | 3.8075 | 2.7572 | 1.2854 | 0.77375 | 0.76172
| WINCHAM T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 5.1327 | 5.1718 | 5.1429 | 5.0157 | 4.881 | 4.7287 | 4.5774 | 4.4176 | 4.266 | 4.0904 | 3.9306 | 3.3222 | 2.5079 | 2.2887 | 2.4341
| WISTASTON HALL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.0306 | 3.346 | 3.3613 | 3.1633 | 2.975 | 2.7521 | 2.4949 | 2.2146 | 1.9257 | 1.6136 | 1.317 | 0.32218 | -1.2558 | -2.2261 | -2.5857
| WRENBURY FRITH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 0.71429 | 0.8458 | 0.82259 | 0.67155 | 0.50783 | 0.31478 | 0.1182 | -0.084117 | -0.29099 | -0.505 | -0.68518 | -1.9787 | -4.0452 | -3.862 | -3.5801
| YOCKINGS GATE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 6.5102 | 6.5284 | 6.4232 | 6.1553 | 5.8193 | 5.4516 | 5.0588 | 4.6113 | 4.1168 | 3.6085 | 3.1297 | 1.5572 | -0.36311 | -0.60454 | -0.22352
| YSBYTY GLAN CLWYD T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.602 | 3.7137 | 3.6943 | 3.4903 | 3.313 | 3.0955 | 2.8844 | 2.6829 | 2.4851 | 2.2665 | 2.0702 | 1.2459 | 0.23216 | 0.14023 | 0.31583
Grid Groups | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 33 | SWANSEA NORTH | 5.4006 | 7.5567 | 7.5977 | 2.0761 | 1.3827 | 5.8457 | -0.17464 | -4.9842 | -10.3993 | -15.4384 | -19.4703 | -33.0927 | -48.6687 | -53.0562 | -50.7883
| HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 18.2377 | 26.4048 | 25.2561 | 19.0592 | 12.2608 | 4.0107 | -4.5772 | -14.0507 | -24.9388 | -35.2163 | -43.9998 | -73.5063 | -106.5262 | -115.1024 | -110.328
| FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 33 | TRAWSFYNYDD | 5.1027 | 5.7817 | 3.9274 | 1.8296 | 9.1959 | 0.093215 | -9.0074 | -19.1087 | -30.8624 | -41.4269 | -49.9086 | -75.3059 | -101.3871 | -104.909 | -102.3826
| COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 33 | CELLARHEAD | 47.6799 | 52.9695 | 29.6183 | 14.7721 | 21.8784 | 4.074 | -6.1155 | -26.789 | -38.787 | -50.6102 | -61.6962 | -104.4975 | -162.2735 | -188.9214 | -187.7418
| GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 33 | KIRKBY | 39.9913 | 42.2717 | 42.3208 | 40.5651 | 39.0609 | 37.043 | 35.0996 | 33.2379 | 31.5476 | 29.5748 | 27.8711 | 19.4121 | 7.7441 | 1.2451 | 3.8001
| GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 33 | LISTER DRIVE | 53.4605 | 55.8876 | 55.9318 | 53.763 | 51.7775 | 49.4137 | 47.1044 | 44.468 | 42.084 | 39.306 | 36.6272 | 26.3897 | 10.3135 | 4.7011 | 5.3332
| FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 33 | KIRKBY | 7.639 | 11.0107 | 10.6505 | 34.7657 | 31.7745 | 27.056 | 20.2708 | 14.677 | 8.9321 | 3.1499 | -1.8959 | -20.8579 | -44.5202 | -55.3873 | -54.9167
| AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 33 | KIRKBY | 13.674 | 16.0398 | 16.0152 | 13.747 | 11.7879 | 9.3638 | 6.8838 | 4.3437 | 1.959 | -0.71361 | -3.179 | -13.1269 | -27.7539 | -34.0084 | -35.1953
| CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 44.2891 | 47.6743 | 47.3548 | 43.1423 | 38.8282 | 33.6166 | 28.3752 | 22.876 | 17.3523 | 11.5227 | 6.4211 | -12.6303 | -37.299 | -47.7512 | -44.3371
| LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 33 | LISTER DRIVE | 47.1083 | 52.5422 | 52.6722 | 50.6487 | 49.0855 | 45.8192 | 43.7583 | 41.8167 | 40.202 | 38.0602 | 36.2027 | 27.1385 | 13.1013 | 11.1299 | 15.5401
| BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 33 | RAINHILL | 42.7313 | 43.4336 | 43.2179 | 42.0915 | 40.9056 | 39.4022 | 37.8515 | 36.1413 | 34.3271 | 32.4338 | 30.7129 | 24.0421 | 14.7499 | 9.2196 | 8.4704
| AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 33 | KIRKBY | 24.4042 | 28.1855 | 27.2267 | 22.1829 | 16.2966 | 10.7889 | 1.3189 | -7.3591 | -16.7136 | -26.2381 | -34.5827 | -65.167 | -102.134 | -116.2988 | -114.2435
| AMLWCH GT1 / CAERGEILIOG GT1 | 33 | WYLFA | 18.4952 | 19.0035 | 17.6718 | 13.0867 | 7.8299 | 1.7679 | -4.4527 | -11.5744 | -19.5821 | -27.2462 | -33.9492 | -55.2341 | -80.9128 | -87.1865 | -85.0752
| HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | 34.3705 | 37.1874 | 36.5923 | 31.7091 | 26.9175 | 21.0845 | 15.1668 | 8.9522 | 2.4454 | -4.1643 | -9.7973 | -30.7805 | -58.7094 | -68.4221 | -67.6885
| BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 33 | RAINHILL | 22.297 | 19.944 | 13.2472 | 9.3627 | 5.6381 | 0.85694 | -3.9395 | -8.8113 | -13.5896 | -18.8386 | -23.4127 | -43.1327 | -69.1534 | -85.1437 | -80.3194
| HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 33 | BIRKENHEAD | 22.8417 | 24.825 | 23.912 | 18.9803 | 13.8199 | 7.5579 | 1.1891 | -5.6765 | -13.0786 | -20.3516 | -26.4763 | -48.0473 | -73.5447 | -83.7282 | -82.9227
| BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 33 | LEGACY | 28.3187 | 31.8011 | 30.3318 | 23.2713 | 17.2039 | 9.6642 | 2.0677 | -9.1252 | -17.1083 | -25.1738 | -32.5899 | -62.7903 | -101.9838 | -117.366 | -138.01
| CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 33 | CAPENHURST | 32.8049 | 36.704 | 35.9218 | 20.5368 | 15.2388 | 8.5324 | 1.5954 | -5.9368 | -13.934 | -21.9944 | -28.9586 | -55.2645 | -88.0972 | -103.145 | -100.4918
| DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 33 | FRODSHAM - INCE | 32.0789 | 35.6577 | 35.1625 | 32.1697 | 30.393 | 27.9344 | 25.2908 | 20.41 | 17.7898 | 15.0604 | -0.62465 | -13.2951 | -31.7772 | -41.6096 | -41.1814
| BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 33 | LISTER DRIVE | 68.4328 | 71.3976 | 71.1691 | 68.69 | 67.0841 | 65.0055 | 62.9915 | 52.823 | 50.7727 | 48.6066 | 46.0292 | 35.354 | 18.3351 | 14.9336 | 19.3305
| BANGOR GT2 / CAERNARFON GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 17.3986 | 20.1065 | 19.6347 | 15.7083 | 11.5778 | 6.7192 | 1.9485 | -3.5709 | -9.4187 | -15.3293 | -20.3667 | -38.3502 | -60.2611 | -66.0629 | -60.14
| DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 33 | CARRINGTON - FIDDLERS FERRY | 16.0845 | 19.0076 | 17.9089 | 13.0267 | 18.7441 | 14.8407 | -2.9749 | -33.6759 | -40.3608 | -47.1835 | -53.4402 | -79.1166 | -112.8329 | -129.7649 | -127.7063
| OSWESTRY GT5 / WHITCHURCH GT1 | 33 | LEGACY | 12.3187 | 14.7014 | 14.2589 | 11.1297 | 7.6906 | 3.7105 | -0.41213 | -4.9906 | -10.2964 | -15.2824 | -20.0267 | -36.2543 | -56.4805 | -61.2811 | -57.4568
| GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 33 | RAINHILL | 28.9061 | 33.0153 | 32.6289 | 28.0006 | 23.1459 | 17.0007 | 10.66 | 3.7428 | -3.4192 | -10.9504 | -17.5704 | -43.3057 | -75.4196 | -86.6294 | -84.2127
| PRENTON GRID GT1 / ROCK FERRY GT1 | 33 | BIRKENHEAD | 20.1231 | 22.5882 | 22.1066 | 21.9194 | 20.9741 | 21.6144 | 7.9302 | 3.4578 | -1.2696 | -6.1183 | -10.4085 | -26.473 | -47.3998 | -58.7475 | -55.7182
| COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 24.674 | 27.7096 | 26.7371 | 21.6208 | 16.2186 | 9.6278 | 2.6449 | -4.8152 | -13.2379 | -21.1117 | -27.5318 | -48.4215 | -73.2711 | -80.4753 | -78.2215
| BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 33 | LISTER DRIVE | 35.3334 | 41.3131 | 42.0998 | 39.4572 | 37.4286 | 34.7698 | 32.2617 | 26.2548 | 24.619 | 22.2346 | 20.0995 | 8.9157 | -7.7962 | -10.7314 | -6.6992
| ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 33 | FRODSHAM - INCE | 29.0962 | 32.9167 | 32.4263 | 28.4025 | 24.7411 | 20.4446 | 16.2961 | 7.1894 | 3.0367 | -1.2438 | -5.1808 | -20.0892 | -38.6344 | -41.5516 | -35.6425
| BOOTLE GT1 / LITHERLAND GT1A | 33 | KIRKBY | 20.6186 | 22.7682 | 22.7222 | 20.4948 | 18.6108 | 16.3421 | 14.1186 | 11.884 | 9.9458 | 7.735 | 5.6822 | -3.1738 | -15.4505 | -19.3328 | -19.0074
| BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 33 | CAPENHURST | -0.21633 | 4.0622 | 17.3877 | 12.8548 | 8.7131 | 3.5799 | -1.4841 | -12.2083 | -17.0774 | -22.252 | -26.8926 | -46.3038 | -71.7088 | -82.7703 | -80.34
| LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 33 | LEGACY | 63.2856 | 66.2077 | 64.4257 | 58.3484 | 50.4924 | 52.5813 | 41.3608 | 29.5025 | 16.1894 | 3.5254 | -7.0959 | -43.2829 | -87.1177 | -100.1422 | -97.7421
| SANKEY BRIDGES GT3 / WARRINGTON GT5 | 33 | CARRINGTON - FIDDLERS FERRY | 6.4157 | 10.058 | 10.1084 | 7.1745 | 4.3694 | 0.90953 | -2.5992 | -6.1468 | -9.5674 | -13.3854 | -16.7481 | -30.0133 | -48.3215 | -54.8195 | -52.8006
| RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 33 | RAINHILL | 25.6959 | 27.7513 | 27.6657 | 25.5419 | 23.4935 | 21.0489 | 18.6278 | 12.6594 | 10.2826 | 7.7 | 5.425 | -3.8892 | -16.7284 | -22.9904 | -21.621
| BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 18.7888 | 26.3446 | 30.8758 | 18.5747 | 17.1491 | 13.5243 | -3.5372 | -7.8349 | -12.1946 | -16.7354 | -20.6166 | -35.5362 | -54.8343 | -62.0573 | -60.5322
| BROMBOROUGH GT3 / ROCK FERRY GT2 | 33 | BIRKENHEAD | 23.5724 | 24.8835 | 24.3692 | 21.3718 | 18.5622 | 15.1354 | 11.7311 | -1.5853 | -5.128 | -8.8522 | -12.1985 | -25.4906 | -41.8506 | -48.529 | -46.3289
| WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 33 | BIRKENHEAD | 34.461 | 38.5572 | 38.8793 | 36.7408 | 34.9112 | 32.5198 | 30.0991 | 27.6054 | 25.1839 | 22.6299 | 20.6054 | 12.3558 | 1.6355 | -1.7883 | -1.7344
| ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | 27.1667 | 28.8637 | 28.2887 | 24.6784 | 20.8295 | 16.354 | 11.8852 | 5.9408 | 1.0184 | -4.0377 | -8.5785 | -25.1161 | -46.9356 | -53.7265 | -52.5877
| HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 33 | RAINHILL | 36.5594 | 36.0295 | 35.8971 | 34.5227 | 33.1724 | 31.4848 | 29.7644 | 27.9929 | 26.2386 | 24.3629 | 22.714 | 15.7439 | 6.4769 | 0.39564 | 1.8448
| DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 12.7574 | 1.7281 | 1.7375 | 0.3389 | -0.80149 | 127.8527 | 126.674 | 125.7035 | 124.9904 | 123.943 | 122.9154 | 117.573 | 109.4602 | 107.9633 | 110.2754

## Low Scenario (Demand)
Demand Headroom (MW)
Return to Contents |  |  |  | Low Scenario
| Group Name | Voltage (kV) | Grid / GSP Group | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050
Primary Groups | ABERDYFI T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 4.5918 | 4.6954 | 4.6604 | 4.429 | 4.1909 | 3.8879 | 3.5977 | 3.2911 | 2.9097 | 2.5766 | 2.3654 | 1.706 | 1.1557 | 0.80055 | 1.0412
| ABERGELE T1 / PENSARN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 1.8776 | 2.0791 | 1.881 | 1.1496 | 0.24473 | 0.42094 | -1.885 | -3.132 | -4.4886 | -5.8069 | -6.9631 | -10.6362 | -14.3534 | -14.3081 | -14.0635
| ABERSOCH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.1224 | 1.0824 | 0.9427 | 0.78559 | 0.10493 | -0.41302 | -0.94582 | -1.5472 | -2.282 | -2.934 | -3.5002 | -4.8613 | -6.6634 | -6.8682 | -6.5503
| ABERYSTWYTH T1 / NORTH RD T1 / PARC-Y-LLYN T1 / PARC-Y-LLYN T2 / U C WALES T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 18.5714 | 19.2506 | 19.1187 | 18.0165 | 16.8978 | 15.4907 | 14.089 | 12.5865 | 11.0434 | 9.4933 | 8.2585 | 3.3016 | -3.358 | -5.8026 | -4.5021
| ACER AVE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 0.20408 | 1.0249 | 1.0939 | 1.964 | 4.3225 | 4.186 | 0.77458 | 0.00089688 | -0.81347 | -1.6126 | -2.326 | -5.0376 | -8.4333 | -11.0376 | -10.9895
| ACORNFIELD RD T1 / DICKINSONS T1 / HAMMOND RD T1 / KODAK T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 14.9898 | 15.4094 | 15.4492 | 14.915 | 14.5562 | 14.1042 | 13.7305 | 13.4763 | 13.3658 | 13.1187 | 12.8874 | 11.1833 | 8.4324 | 7.7068 | 8.4006
| ACTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4082 | 2.6257 | 2.5972 | 2.3592 | 2.1036 | 1.7881 | 1.4702 | 1.1224 | 0.7594 | 0.37407 | 0.054845 | -1.2453 | -2.9499 | -3.9905 | -3.5746
| AIGBURTH VALE T1 / IVY AVE T1 / MATHER AVE T1 / MOSSLEY HILL T1 / WAVERTREE T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 18.1429 | 19.3926 | 19.475 | 18.7173 | 17.9867 | 17.1014 | 16.1349 | 15.1049 | 14.0723 | 12.9105 | 11.8942 | 8.1996 | 2.6869 | 0.15171 | -0.51005
| AINSDALE T1 / PINFOLD LA T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 2.6612 | 2.8948 | 2.782 | 2.2527 | 1.6736 | 0.96991 | 0.23828 | -0.57282 | -1.4763 | -2.3371 | -3.0854 | -5.5314 | -8.2806 | -8.8305 | -8.8633
| AINTREE LOCAL T1 / OLD ROAN T1 / WANGO LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 8.0918 | 8.4335 | 8.3528 | 7.5856 | 6.916 | 6.1149 | 5.327 | 4.4909 | 3.7299 | 2.9094 | 2.1557 | -0.89002 | -5.0803 | -6.8198 | -7.4131
| AIRBUS T1 / BROUGHTON RETAIL PARK T1 / MIXALLOY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 12.8469 | 13.0545 | 13.01 | 12.621 | 12.2458 | 11.7793 | 11.3156 | 10.8524 | 10.3731 | 9.8667 | 9.3957 | 7.5078 | 5.0887 | 4.4785 | 4.7372
| AIRPORT T1 / ALDERWOOD AVE (CROYDE RD) T1 / HAREFIELD RD T1 / METAL BOX (SPEKE) T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 19.5408 | 19.7952 | 19.7055 | 19.1733 | 18.6036 | 17.9723 | 17.3587 | 16.7127 | 16.0647 | 15.3686 | 14.6621 | 12.1746 | 8.3268 | 7.4808 | 7.8792
| ALBERT DOCK T1 / KINGS DOCK T1 / KINGS DOCK T2 / WAPPING T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 23.2959 | 23.5075 | 23.5176 | 23.2878 | 23.109 | 22.8869 | 22.7051 | 22.5441 | 22.4258 | 22.2571 | 22.0852 | 21.2586 | 19.8582 | 19.5727 | 19.9735
| ALLERTON T1 / ECP WEST-BANKS RD T1 / GARSTON T1 / WEAVER IND EST T1 / YEW TREE RD T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 22.9694 | 23.5261 | 23.5519 | 23.0241 | 22.5933 | 22.0679 | 21.5894 | 20.8202 | 20.216 | 19.4714 | 18.6987 | 15.8257 | 10.9892 | 9.1876 | 9.5907
| ALMATEX T1 / ST HELENS WWTW T1 / WATERY LA T2 / ex DELTA METALS T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 8.5367 | 8.9039 | 8.8829 | 8.5438 | 8.2351 | 7.8763 | 7.5301 | 7.2063 | 6.8924 | 6.5254 | 6.1547 | 4.6426 | 2.2341 | 1.6873 | 2.1747
| ALMONDS TURN T1 / ATLANTIC COMPLEX T1 / GIRO T1 / MIDLAND BANK T1 / NETHERTON T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 22.6735 | 23.0345 | 22.7325 | 21.7106 | 20.5033 | 19 | 17.4626 | 15.7357 | 13.8385 | 11.8405 | 10.0308 | 2.9076 | -6.1247 | -7.4995 | -6.1882
| ALPOCO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.2755 | 5.3357 | 5.3188 | 5.1905 | 5.0645 | 4.9209 | 4.7748 | 4.6154 | 4.4558 | 4.2964 | 4.1543 | 3.6553 | 3.0438 | 2.9314 | 2.9741
| AMLWCH T1 / AMLWCH T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 6.8469 | 6.7775 | 6.6305 | 6.1869 | 5.6721 | 5.0812 | 4.4708 | 3.7891 | 3.0036 | 2.2753 | 1.6575 | -0.18355 | -2.0992 | -2.2464 | -2.0129
| ANDERTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.6224 | 3.5918 | 3.3998 | 2.8801 | 2.5599 | 2.0285 | 0.71325 | -0.16709 | -1.1999 | -2.1772 | -3.0336 | -5.7757 | -8.9554 | -9.0157 | -8.9089
| APPLETON T1 / HORNSBRIDGE T1 / LUGSDALE T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 3.4694 | 4.1529 | 4.0447 | 3.1655 | 3.4561 | 4.7681 | -0.11072 | -1.3373 | -2.5919 | -3.9187 | -5.0753 | -9.8609 | -16.2257 | -20.5717 | -20.0883
| ARROWE PK HOSP T1 / CHAMPION PLUGS T1 / CHAMPION PLUGS T2 / WOODCHURCH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 20.5612 | 20.7962 | 20.7853 | 20.4098 | 20.1194 | 19.7834 | 19.4683 | 19.2121 | 19.0012 | 18.7141 | 18.414 | 17.0558 | 14.7852 | 14.1617 | 14.6467
| ARUNDEL T1 / GROVE PK T1 / WAVERTREE VALE T1 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 7.1735 | 7.88 | 7.9668 | 7.6922 | 7.4864 | 7.1919 | 6.8812 | 6.5796 | 6.2514 | 5.907 | 5.6764 | 4.7221 | 3.5636 | 3.5261 | 3.9698
| ASH RD T1 / KELLOGGS (WREXHAM) T1 / KELLOGGS (WREXHAM) T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.9388 | 4.3398 | 4.3154 | 3.695 | 3.1951 | 2.6184 | 2.1209 | 1.6755 | 1.3603 | 0.91978 | 0.53019 | -1.4201 | -4.4792 | -5.1749 | -4.2889
| ASSOCIATED LEAD T1 / GREAT BOUGHTON T1 / PIPERS ASH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 7.4898 | 7.9541 | 7.658 | 6.6017 | 5.3498 | 3.8327 | 2.2131 | 0.36719 | -1.6907 | -3.7052 | -5.4825 | -11.499 | -18.2388 | -18.923 | -18.6725
| ASTMOOR IND EST T1 / MACKAMAX T1 / MERSEY RD T1 / PICOW FARM RD T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 18.6939 | 19.0556 | 18.9952 | 18.5397 | 18.2772 | 17.9151 | 17.5908 | 17.3044 | 17.0782 | 16.7949 | 16.4928 | 14.8772 | 12.3143 | 11.1157 | 11.2477
| ATHOL ST T1 / CHISENHALE ST T1 / SANDHILLS LA T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 9.5531 | 9.6966 | 9.6173 | 9.2264 | 8.8141 | 8.5059 | 8.1279 | 7.7259 | 7.3091 | 6.8482 | 6.4027 | 4.8421 | 2.3214 | 1.9137 | 2.4512
| AUDLEM T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.8673 | 3.9957 | 3.9168 | 3.6792 | 3.3708 | 3.0391 | 2.6727 | 2.2535 | 1.7753 | 1.3051 | 0.89304 | -0.26262 | -1.6982 | -1.9868 | -1.6562
| BALA T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.0204 | 4.0431 | 3.9303 | 3.5216 | 3.0583 | 2.5126 | 1.9672 | 1.3516 | 0.60705 | -0.047534 | -0.55458 | -1.9184 | -3.1139 | -3.0159 | -2.6874
| BANASTRE RD T1 / DOVER RD T1 / GRANTHAM CL T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | -1.8898 | 9.5885 | 9.5467 | 8.9156 | 8.2969 | 7.5526 | 6.7673 | 5.907 | 5.0367 | 4.1419 | 3.3023 | 0.25629 | -3.9758 | -5.7786 | -6.5748
| BANGOR HOSP T1 / BANGOR UNIVERSITY T1 / EITHINOG T1 / HIRAEL T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 16.8673 | 17.3639 | 17.3192 | 16.6688 | 16.0833 | 15.3335 | 14.6123 | 13.9046 | 13.2093 | 12.491 | 11.9131 | 9.3516 | 6.2044 | 4.6725 | 5.2666
| BARBAULD ST T1 / HORROCKS LA T1 / WARRINGTON CENTRAL T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 11.1837 | 11.3211 | 11.2368 | 10.806 | 10.3896 | 9.9327 | 9.5111 | 9.0776 | 8.6428 | 8.1487 | 7.6708 | 5.9571 | 3.118 | 2.6067 | 3.32
| BARMOUTH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.0204 | 5.047 | 4.9558 | 4.6955 | 4.3767 | 4.0058 | 3.6261 | 3.1989 | 2.6815 | 2.2114 | 1.8265 | 0.70889 | -0.38203 | -0.20431 | 0.13267
| BARNSTON T1 / GAYTON T1 / IRBY T1 / THINGWALL T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 12.1531 | 12.6991 | 12.3616 | 10.7948 | 9.043 | 6.9463 | 4.7773 | 2.3773 | -0.22951 | -2.7753 | -4.9518 | -12.2405 | -20.3348 | -22.2781 | -22.4534
| BASCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.6224 | 1.8992 | 1.8829 | 1.591 | 1.2793 | 0.90385 | 0.51804 | 0.09711 | -0.32854 | -0.75657 | -1.1363 | -2.5668 | -4.5594 | -5.5751 | -5.5284
| BASS CHARRINGTON T1 / BASS CHARRINGTON T2 / CLIFTON T1 / YKK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 13.8673 | 14.4737 | 14.479 | 13.8432 | 13.2966 | 12.6009 | 11.9534 | 11.3321 | 10.819 | 10.1762 | 9.5725 | 6.7668 | 2.6101 | 0.58637 | 0.96931
| BATTERSBY LA T1 / RYLANDS ELDON ST T2 | 6 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 8.1102 | 8.1603 | 8.1369 | 8.0836 | 8.0498 | 8.0131 | 7.9577 | 7.8747 | 7.7794 | 7.69 | 7.5961 | 7.2942 | 6.8311 | 6.6536 | 6.6983
| BEAUMARIS T1 / BEAUMARIS T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.9739 | 3.9482 | 3.7985 | 3.4163 | 2.9392 | 2.4225 | 1.8958 | 1.2804 | 0.56805 | -0.10258 | -0.7073 | -2.1373 | -4.1951 | -4.4855 | -4.0127
| BEAUMONT ST T1 / DINGLE VALE T1 / LARK LA T1 / MDHB BRUNSWICK DOCK T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 8.7143 | 10.0861 | 9.7141 | 9.3779 | 9.1923 | 8.2848 | 7.9947 | 7.7645 | 7.6636 | 7.4153 | 7.2178 | 5.7191 | 3.2465 | 2.8301 | 3.8442
| BEDBURN DV T1 / BLUEBELL LA T1 / BROOKBRIDGE T1 / ECCLESTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 12.5816 | 13.3043 | 13.0715 | 11.7035 | 10.106 | 8.0886 | 5.9591 | 3.5319 | 0.88921 | -1.8114 | -4.1987 | -13.0293 | -22.6949 | -23.3244 | -22.0593
| BEECH ST T1 / LISTER DV A T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 4.5469 | 4.7749 | 4.8039 | 4.6792 | 4.5983 | 4.4827 | 4.3738 | 4.2759 | 4.2007 | 4.0996 | 4.0036 | 3.5198 | 2.8101 | 2.6312 | 2.7097
| BEMROSE T1 / CARR LA EAST T1 / LUCAS (FAZAKERLEY) T1 / NORRIS GREEN T1 / WEST DERBY T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 17.8163 | 18.7732 | 18.7428 | 17.8012 | 17.0011 | 16.0164 | 14.9827 | 13.941 | 12.9241 | 11.7905 | 10.7481 | 6.7838 | 0.76684 | -2.3425 | -3.0993
| BENTINCK ST T1 / BENTINCK ST T2 / CHESTER ST T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 10.2612 | 10.3122 | 10.1659 | 9.5654 | 8.9782 | 10.1284 | 9.5009 | 8.8322 | 8.1004 | 7.3872 | 6.723 | 4.4192 | 1.3294 | 0.77873 | 0.90657
| BERSHAM COLLIERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 1.602 | 1.6863 | 1.6786 | 1.5372 | 1.4082 | 1.2387 | 1.0621 | 0.89679 | 0.71249 | 0.53636 | 0.38436 | -0.26846 | -1.1133 | -1.5643 | -1.5506
| BERSHAM RD T1 / IND COOPE T1 / RHYD BROUGHTON LA T1 / TUTTLE ST T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 14.1939 | 14.8153 | 14.721 | 13.8895 | 13.1701 | 12.2299 | 11.3002 | 10.3665 | 9.4387 | 8.4909 | 7.7123 | 4.2765 | 0.10376 | -2.38 | -1.4292
| BETHESDA T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 3 | 3.1731 | 3.1226 | 2.8404 | 2.5297 | 2.1306 | 1.729 | 1.3042 | 0.82994 | 0.34929 | -0.031559 | -1.4381 | -3.1023 | -4.1618 | -3.7504
| BETWS-Y-COED T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.9694 | 3.8968 | 3.7365 | 3.2353 | 2.6691 | 2.0132 | 1.3796 | 0.65201 | -0.21886 | -0.98833 | -1.6047 | -3.1464 | -4.7857 | -4.8651 | -4.5861
| BEWSEY T1 / OWEN ST T1 / RODNEY ST T1 / RYLANDS ELDON ST T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 13.8061 | 14.3234 | 14.2777 | 13.5333 | 12.8486 | 12.0455 | 11.2768 | 10.5074 | 9.7709 | 8.9646 | 8.2248 | 5.282 | 0.93179 | -0.22194 | 0.17834
| BIBBYS T1 / INLAND REVENUE OFFICES T1 / REGENT RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 5.6224 | 6.1282 | 6.1519 | 8.1595 | 7.7649 | 7.3738 | 6.9657 | 5.6876 | 5.3745 | 4.988 | 4.6524 | 3.0399 | 0.92388 | 0.48121 | 0.5735
| BICC HUYTON QUARRY T1 / TARBOCK T1 / WHISTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 11.7143 | 11.8798 | 11.7103 | 11.0796 | 10.3303 | 9.4286 | 8.5113 | 7.4742 | 6.3749 | 5.2241 | 4.1635 | 0.12208 | -4.8624 | -5.2381 | -4.7833
| BICC WREXHAM T1 / MARCHWIEL T1 / WIE CENTRAL T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 6.898 | 7.2789 | 7.3074 | 6.8654 | 6.5842 | 6.2315 | 5.9471 | 5.7621 | 5.7099 | 5.5378 | 5.3558 | 4.0186 | 1.7885 | 1.2641 | -22.9798
| BIRKENHEAD CENTRAL T1 / SINGLETON AVE T1 / TRANMERE T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 9.5673 | 9.7948 | 9.7368 | 9.3454 | 8.8776 | 8.4985 | 8.1263 | 7.5841 | 7.0502 | 6.4791 | 5.8851 | 3.6811 | 0.57209 | -0.26798 | -0.1315
| ex BIXTETH ST T1 / LITTLEWOODS T1 / PALL MALL T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 3.8633 | 3.9715 | 3.9258 | 3.7187 | 3.4693 | 3.2141 | 2.9552 | 2.6844 | 2.4034 | 2.0812 | 1.7607 | 0.70724 | -1.0602 | -1.3276 | -0.87567
| BLACON T1 / COCOA BARRY T1 / CRANE BANK T1 / KNUTSFORD WAY T1 / TOWER WHARF T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 16.2245 | 17.0705 | 16.993 | 16.0245 | 15.091 | 13.8883 | 12.7012 | 11.4745 | 10.3116 | 9.0481 | 7.9512 | 2.9866 | -3.492 | -7.5034 | -6.3265
| BLAENAU FFESTINIOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.6939 | 1.7945 | 1.7716 | 1.6491 | 1.5194 | 1.3468 | 1.1739 | 0.98944 | 0.78203 | 0.57317 | 0.40677 | -0.26892 | -0.9166 | -1.2601 | -0.92045
| BLUNDELL ST T1 / ROPEWALKS T1 / ST JAMES T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 9.0198 | 9.4276 | 9.4701 | 9.2325 | 9.0902 | 8.8885 | 8.723 | 8.6236 | 8.6088 | 8.5213 | 8.4313 | 7.6166 | 6.2072 | 5.8705 | 6.3598
| BLUNDELLSANDS (NORTH) T1 / BLUNDELLSANDS (SOUTH) T1 / CROSBY T1 / KERSHAW AVE T1 / WATERLOO T2 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 15.9898 | 16.8645 | 16.5027 | 14.999 | 13.1904 | 10.958 | 8.5995 | 5.9389 | 3.007 | 0.0033533 | -2.6363 | -12.1456 | -23.1013 | -24.9578 | -23.5844
| BODFARI PRODUCERS T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.6122 | 4.7189 | 4.7298 | 4.6451 | 4.5911 | 4.5137 | 4.4598 | 4.4059 | 4.3906 | 4.35 | 4.3031 | 3.9994 | 3.4633 | 3.2851 | 3.4067
| BOLTON ST T1 / GREEK ST T1 / HPO COPPERAS HILL T1 / OLDHAM PLACE T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.8061 | 5.322 | 5.3686 | 4.8722 | 4.5729 | 4.1868 | 3.8984 | 3.6806 | 3.5769 | 3.3783 | 3.1691 | 1.7763 | -0.50424 | -1.0937 | -0.4975
| BOOTLE GRID T1 / KELLOGGS T1 / PACIFIC RD T1 / WASHINGTON ST T1 / WATERLOO T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | 18.4388 | 19.0863 | 19.0625 | 18.1407 | 17.3505 | 16.3744 | 15.4431 | 14.4966 | 13.6885 | 12.7763 | 11.9545 | 8.1682 | 3.2825 | 1.9062 | 1.7232
| BOOTLE GRID T2 / ORRELL MOUNT T1 / SCARISBRICK AVE T1 / TATTON RD T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | 14.4082 | 15.1102 | 15.0068 | 14.1783 | 13.4239 | 12.5305 | 11.5774 | 10.5425 | 9.5051 | 8.3922 | 7.3383 | 3.4999 | -2.0912 | -4.3621 | -4.7933
| BOTWNNOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.2041 | 5.2757 | 5.2386 | 5.0684 | 4.8752 | 4.6561 | 4.4271 | 4.18 | 3.888 | 3.6321 | 3.4388 | 2.8715 | 2.1685 | 1.8551 | 1.9124
| BOULEVARD T1 / CHAPELFORD T1 / HAWLEYS LA T1 / WESTBROOK T1 / WINWICK QUAY T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 16.2857 | 17.0362 | 16.9741 | 15.9736 | 15.0498 | 13.908 | 12.8038 | 11.7103 | 10.7267 | 9.6012 | 8.5817 | 4.1822 | -2.1246 | -5.6333 | -5.2446
| BOW ST T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.6735 | 2.8102 | 2.7048 | 2.3107 | 1.8162 | 1.6302 | 0.6699 | -0.014426 | -0.75819 | -1.4864 | -2.1373 | -4.213 | -6.5414 | -6.9139 | -6.7467
| BOWATER CONTAINERS T1 / ELLESMERE PORT LOCAL T1 / HH ROBERTSONS T1 / MOBIL OIL (E PORT) T1 / WHITBY T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 6.9082 | 7.5628 | 7.491 | 6.5913 | 5.9128 | 5.032 | 4.2098 | 3.4165 | 2.6681 | 1.8516 | 1.0952 | -2.2152 | -7.1578 | -9.4975 | -9.9555
| BR STATION T1 / DUCHY RD T1 / ELECTRA WAY T1 / MIDLAND ROLLMAKERS T1A / NORTH WESTERN MILLS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 12.7347 | 13.4245 | 8.3114 | 7.1533 | 6.2604 | 1.02 | -0.045426 | -1.0696 | -1.9647 | -2.9807 | -3.9671 | -8.7727 | -15.3189 | -18.3967 | -17.4973
| BRD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.1327 | 2.2712 | 2.2152 | 1.8347 | 1.4547 | 0.99691 | 0.54103 | 0.053123 | -0.45382 | -0.9498 | -1.358 | -3.2613 | -6.3264 | -6.4303 | -6.3014
| BRITISH ALUMINIUM LATCHFORD T1 / GREENHALL WHITLEY T1 / LATCHFORD T1 / LATCHFORD T2 / THAMES BOARD MILL T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 11.8367 | 12.7118 | 12.7782 | 12.1513 | 11.655 | 11.0288 | 10.4127 | 9.8525 | 9.3878 | 8.7955 | 8.272 | 5.7763 | 1.9924 | 0.6271 | 0.80638
| BRITISH OXYGEN T1 / WINDLEHURST T1 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 2.8041 | 3.1316 | 3.4826 | 3.5885 | 2.6338 | 2.3589 | 2.0608 | 0.20406 | -0.14612 | -0.53873 | -0.90969 | -2.1509 | -4.1886 | -4.8133 | -4.5912
| BRITISH PIPE ASSOCIATION T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 3.9388 | 4.0355 | 4.0263 | 3.8903 | 3.7725 | 3.617 | 3.4949 | 3.3954 | 3.3077 | 3.1829 | 3.0672 | 2.5425 | 1.659 | 1.4776 | 1.6927
| BRITISH SIDAC T1 / SHERDLEY RD T1 / ST HELENS LINKWAY T1 / WATERY LA T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 9.6592 | 9.8972 | 9.7723 | 21.0479 | 20.4633 | 19.728 | 19.0107 | 18.2448 | 17.4579 | 16.6504 | 15.9481 | 12.9201 | 9.2033 | 6.2731 | 7.238
| BROADGREEN T1 / CROXTETH T1 / EAST PRESCOT RD (FINCH LA) T1 / KNOTTY ASH T1 / LEYFIELD RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 12.102 | 13.6078 | 13.7149 | 12.77 | 11.948 | 10.9008 | 9.8035 | 8.6716 | 7.6212 | 6.4025 | 5.3115 | 0.95002 | -5.5501 | -8.5093 | -9.1356
| BROMFIELD T1 / BROMFIELD T2 / PONTERWYL T1 / RHYD-Y-GOLEU T1 / SYNTHITE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 22.1224 | 22.7348 | 22.6305 | 21.6112 | 20.6114 | 19.3745 | 18.1337 | 16.8104 | 15.4724 | 14.1119 | 12.9619 | 8.6147 | 3.2234 | 0.35243 | 0.0086098
| BROOK LA T1 / MANNINGS LA T1 / NEWTOWN CHESTER T1 / UPTON HEATH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 12.1327 | 13.0414 | 12.8734 | 11.9121 | 10.9252 | 9.6426 | 8.2538 | 6.7316 | 5.1102 | 3.4748 | 2.0342 | -3.519 | -9.8452 | -13.7626 | -13.01
| BROOK ST T1 / KINGSWAY TUNNEL T1 / NWWA SANDON DOCK T1 / NWWA SANDON DOCK T2 | 11 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 17.1224 | 17.4849 | 17.49 | 17.0292 | 16.68 | 16.3639 | 16.0629 | 15.8198 | 15.675 | 15.4432 | 15.1886 | 13.7507 | 11.4267 | 10.8917 | 11.3679
| BRYN STANLEY T1 / DENBIGH T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.2857 | 4.4472 | 4.3772 | 3.9621 | 3.5486 | 3.0393 | 2.5104 | 1.9663 | 1.3823 | 0.79187 | 0.2849 | -1.6311 | -4.0332 | -4.9788 | -4.8435
| BUCKINGHAM ST T1 / EVERTON RD T1 / SUBURBAN RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 8.6633 | 9.221 | 9.3161 | 9.1642 | 9.0786 | 8.9061 | 8.7862 | 8.6882 | 8.6608 | 8.5755 | 8.4978 | 7.9059 | 7.0419 | 6.9425 | 7.2747
| BUCKLEY T1 / BUCKLEY T2 / BUCKLEY CROSS T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 8.4694 | 8.9653 | 8.8543 | 8.0374 | 7.1774 | 6.126 | 5.0481 | 3.8529 | 2.6637 | 1.4437 | 0.38679 | -3.5705 | -8.514 | -11.3803 | -11.7923
| BUILDWAS RD T1 / MORGAN REFRACTORIES T1 / NESTON MAIN T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 11.1735 | 11.2759 | 11.0434 | 10.1695 | 9.1646 | 7.9928 | 6.7974 | 5.4503 | 3.9899 | 2.5526 | 1.312 | -2.7953 | -7.3816 | -7.5949 | -7.4217
| BURLINGTON AVE T1 / FRESHFIELD T1 / MARSH BROWS T1 / SOUTHPORT RD T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 13 | 13.5936 | 13.4215 | 12.3469 | 11.2102 | 9.8356 | 8.3983 | 6.831 | 5.25 | 3.6168 | 2.1806 | -3.022 | -9.4521 | -13.2276 | -13.6262
| BURMAH OIL T1 / CABOT CARBON T1 / VAN LEER NO 1 T1 | 7 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 1.7673 | 1.9047 | 1.9159 | 1.776 | 1.6727 | 1.5452 | 1.455 | 1.3824 | 1.3641 | 1.3018 | 1.2415 | 0.75809 | -0.076011 | -0.33285 | -0.11709
| BUTLINS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.5306 | 4.661 | 4.6772 | 4.5891 | 4.5323 | 4.448 | 4.3715 | 4.3142 | 4.2699 | 4.1956 | 4.137 | 3.8159 | 3.3189 | 3.1286 | 3.289
| BUTTINGTON CROSS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.398 | 3.5391 | 3.5269 | 3.3546 | 3.2344 | 3.0666 | 2.9166 | 2.785 | 2.6674 | 2.5338 | 2.4038 | 1.7397 | 0.80071 | 0.48639 | 0.53043
| BXL BROMBOROUGH T1 / TULIP T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 3.2551 | 3.4041 | 3.3961 | 3.0591 | 2.8179 | 2.5143 | 2.2508 | 2.0213 | 1.8407 | 1.6244 | 1.4127 | 0.31911 | -1.1869 | -1.4749 | -1.2715
| CABLE ST T1 / GRADWELL ST T2 / OLDHAM PLACE T2 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 5.6837 | 6.222 | 6.2889 | 5.8874 | 5.6385 | 5.3409 | 5.1166 | 4.9535 | 4.6926 | 4.5218 | 4.0954 | 2.1059 | -1.1539 | -1.0965 | -0.14953
| CABLE ST T2 / CROWN COURTS T1 / GRADWELL ST T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 10.2653 | 10.3968 | 10.2803 | 9.6591 | 9.291 | 8.7991 | 8.3172 | 7.8636 | 7.4142 | 6.9191 | 6.4339 | 4.7639 | 2.2138 | 2.2456 | 3.1954
| CADBURYS KRONOSPAN T1 / CADBURYS KRONOSPAN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.6531 | 3.8505 | 3.7881 | 3.4444 | 3.095 | 2.663 | 2.2333 | 1.7911 | 1.3332 | 0.84719 | 0.42227 | -1.203 | -3.3469 | -3.504 | -3.1481
| CADBURYS T1 / CADBURYS T2 / HOPFIELD RD T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 8.7551 | 9.2658 | 9.2688 | 8.8454 | 8.5448 | 8.1483 | 7.7617 | 7.3832 | 7.0493 | 6.6594 | 6.3169 | 4.7114 | 2.4001 | 1.6496 | 1.8762
| CAERGEILIOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5 | 3.5319 | 3.4243 | 3.0548 | 2.5253 | 2.0444 | 1.5445 | 0.81672 | -0.012176 | -0.81873 | -1.57 | -3.9002 | -6.6807 | -7.2958 | -7.0639
| CAERGWRLE T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 1.5816 | 1.7758 | 1.6795 | 1.3363 | 2.3113 | 2.4185 | -1.0555 | -2.0191 | -3.0852 | -4.165 | -5.1352 | -8.2258 | -11.8443 | -12.4591 | -12.1503
| CAERNARFON T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 1.9592 | 2.1204 | 2.0757 | 1.7836 | 1.464 | 1.0958 | 0.7367 | -0.073456 | -0.806 | -1.5832 | -2.3443 | -4.9936 | -8.2418 | -8.6225 | -8.2849
| CAERSWS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 4.3469 | 4.4511 | 4.407 | 4.1632 | 3.8868 | 3.5647 | 3.2218 | 2.8621 | 2.4391 | 2.0589 | 1.7439 | 0.72959 | -0.51855 | -0.79815 | -0.74157
| CALDY T1 / HOYLAKE T1 / MEOLS T1 / WEST KIRBY SOUTH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 14.6531 | 15.1977 | 15.0053 | 13.6966 | 12.4428 | 10.8441 | 9.2719 | 7.6215 | 5.7556 | 4.0259 | 2.7122 | -1.7953 | -6.9589 | -10.5381 | -10.5301
| CARBORUNDUM T1 / HOUGHTONS LA T1 / RAINFORD T1 / WINDLEHURST T2 | 11 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 12.8469 | 13.5638 | 13.4242 | 12.3248 | 11.1613 | 9.7506 | 8.3074 | 6.7511 | 5.1892 | 3.5582 | 2.1271 | -3.4933 | -10.8454 | -15.5879 | -15.5776
| CARLTON ST T1 / CARLTON ST T2 / CHALON WAY T2 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 8.2 | 8.5116 | 8.4886 | 8.0253 | 7.6581 | 7.1978 | 6.7814 | 6.3967 | 6.0332 | 5.6456 | 5.3146 | 3.7503 | 1.5271 | 0.70349 | 0.78405
| CARMEL T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.051 | 1.1827 | 1.1194 | 0.95707 | 0.70611 | 0.42435 | 0.11298 | -0.26258 | -0.69507 | -1.1308 | -1.5322 | -2.7486 | -4.2254 | -4.2818 | -3.9053
| CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 11 | CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 16.9592 | 17.9007 | 17.9095 | 16.8407 | 15.9052 | 14.732 | 13.5755 | 12.4004 | 11.2208 | 10.0009 | 9.0038 | 5.2538 | 0.10686 | -2.1492 | -2.7243
| CEFN MAWR T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.9388 | 3.9891 | 3.8488 | 3.417 | 2.8902 | 2.2989 | 1.6878 | 1.0013 | 0.17125 | -0.59584 | -1.2501 | -3.0402 | -5.1414 | -5.7333 | -5.9245
| CEMAES BAY T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 2.2959 | 2.2827 | 2.1963 | 1.9761 | 1.7134 | 1.4238 | 1.112 | 0.76263 | 0.35786 | -0.012856 | -0.34525 | -1.276 | -2.3409 | -2.4953 | -2.35
| CEMMAES RD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.4898 | 1.5321 | 1.4572 | 1.0755 | 0.70339 | 0.3514 | -0.18676 | -0.67694 | -1.2645 | -1.7703 | -2.1646 | -3.4482 | -4.6355 | -4.9647 | -5.4786
| CEREAL PARTNERS T1 / LEVER GEORGIA AVE T1 / POOL LA T1 / UML LEVER BROMBOROUGH T2 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 20.6224 | 20.893 | 20.9103 | 20.5851 | 20.3486 | 20.0506 | 19.8168 | 19.6439 | 19.5521 | 19.3669 | 19.1866 | 18.0791 | 16.1788 | 15.5264 | 15.8643
| CHALON WAY T1 / TECHNOLOGY CAMPUS T1 / WOODVILLE ST T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 1.5898 | 2.7356 | 2.7027 | 2.2857 | 1.9021 | 1.4502 | 1.0121 | 0.56577 | 0.14548 | -0.3161 | -0.75657 | -2.5703 | -5.0929 | -6.1193 | -6.5416
| CHESHIRE GREEN T1 / NWF T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 4.3265 | 4.4409 | 4.3817 | 4.0581 | 3.8147 | 3.511 | 3.2209 | 2.9663 | 2.7254 | 2.4645 | 2.2141 | 1.05 | -0.58533 | -1.2413 | -1.082
| CHESTER GATES T1 / UNILEVER DUNKIRK T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 4.2245 | 17.8703 | 17.8689 | 17.6194 | 17.4238 | 17.1701 | 16.9711 | 16.567 | 16.4094 | 16.2273 | 16.0646 | 15.2792 | 14.1221 | 13.735 | 13.9133
| CHESTER ST (WREXHAM) T1 / EAGLES MEADOW T1 / RHOSNESNI T1 / WHITEGATE T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 16.2143 | 16.8242 | 16.7066 | 15.9161 | 15.1064 | 14.0619 | 12.9884 | 11.852 | 10.6722 | 9.4928 | 8.5148 | 4.4671 | -0.29409 | -3.4826 | -2.7749
| CHILDWALL T1 / CHILDWALL FIVEWAYS T1 / LYNDENE RD T1 / MIDDLEMASS HEY T1 / NAYLORS RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 13.4898 | 14.7165 | 14.6661 | 13.601 | 12.5226 | 11.1113 | 9.6997 | 8.2089 | 6.6902 | 5.0882 | 3.7545 | -1.8388 | -9.1069 | -14.29 | -12.8237
| CHOWLEY T1 / CHOWLEY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.2143 | 3.4807 | 3.4253 | 2.9986 | 2.5419 | 1.9955 | 1.4263 | 0.80565 | 0.17708 | -0.45869 | -0.99305 | -3.0205 | -5.6266 | -6.9709 | -6.9501
| CHURCH LA T1 / NANT HALL T1 / PRESTATYN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 10.5102 | 10.8644 | 10.7118 | 9.9573 | 9.1051 | 8.0654 | 6.998 | 5.7923 | 4.4702 | 3.2201 | 2.1698 | -1.2073 | -4.6258 | -5.0413 | -4.8896
| CHURCH LAWTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.7347 | 3.8988 | 3.806 | 3.4847 | 3.177 | 2.7721 | 2.3453 | 1.8622 | 1.328 | 0.81876 | 0.35234 | -1.2987 | -3.1352 | -4.3149 | -4.4513
| CHURCH ST WINSFORD T1 / OVER T1 / WHARTON PK T1 / WOODFORD PK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 11.8061 | 12.5961 | 12.495 | 11.4093 | 10.2878 | 8.8851 | 7.4608 | 5.9591 | 4.4012 | 2.8504 | 1.572 | -3.4114 | -9.5037 | -13.3953 | -13.0161
| CIVIC CENTRE T1 / CLAUGHTON AVE T1 / ELECTRICITY ST T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.4147 | 12.4111 | 12.0839 | 11.0935 | 10.5274 | 9.7646 | 8.9589 | 8.087 | 7.1683 | 6.3863 | 5.542 | 1.9874 | -2.772 | -5.3134 | -5.8318
| CLEDFORD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.4184 | 1.8284 | 1.8503 | 1.6106 | 1.3907 | 1.1129 | 0.79721 | 0.47175 | 0.13383 | -0.2291 | -0.54543 | -1.7467 | -3.4376 | -4.6528 | -4.6346
| CLOCKFACE T1 / GEC ST HELENS T1 / HILLS MOSS T1 / NCB SUTTON MANOR T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 16.898 | 17.2855 | 17.1829 | 16.4675 | 15.7609 | 14.8824 | 14.0309 | 13.175 | 12.3391 | 11.4213 | 10.6241 | 7.1223 | 2.3572 | -0.85219 | -0.10779
| CLUBMOOR T1 / DUNLOPS WALTON T1 / WALTON T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 10.1531 | 10.3547 | 10.3656 | 10.1032 | 9.9348 | 9.7701 | 9.6234 | 9.5158 | 9.4743 | 9.3682 | 9.2633 | 8.5542 | 7.3616 | 7.0595 | 7.3839
| CLUBMOOR T2 / LISTER DV A T1 / SUBURBAN RD T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 6.5202 | 7.0173 | 7.0739 | 6.8211 | 6.6172 | 6.352 | 6.0955 | 5.6041 | 5.4039 | 5.141 | 4.9043 | 3.7626 | 2.0907 | 1.7519 | 2.0089
| COEDPOETH T1 / COEDPOETH T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.4592 | 4.6088 | 4.4819 | 4.0561 | 3.528 | 3.9215 | 2.2338 | 1.4813 | 0.64659 | -0.15698 | -0.84801 | -3.2986 | -5.4569 | -4.5284 | -3.6191
| COLWYN BAY T1 / COLWYN BAY T2 / RHOS-ON-SEA T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 11.2041 | 11.5086 | 11.5046 | 11.1959 | 10.9368 | 10.6134 | 10.2797 | 9.961 | 9.6426 | 9.2848 | 8.9622 | 7.3723 | 4.0045 | 3.2844 | 3.29
| CONEY GREEN T1 / OSWESTRY T2 / OSWESTRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 8.3571 | 9.3321 | 9.3444 | 9.0119 | 8.6467 | 8.1445 | 7.5777 | 6.9525 | 6.2326 | 5.5086 | 4.9491 | 2.7799 | 0.10001 | -2.1122 | -1.5163
| CONIX T1 / CONIX T2 / MEDEVA T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 12.6939 | 12.9104 | 12.9215 | 12.6892 | 12.5294 | 12.3374 | 12.181 | 12.0845 | 12.0497 | 11.959 | 11.8571 | 11.0897 | 9.7776 | 9.4076 | 9.7579
| CONNAHS QUAY LOCAL T1 / CONNAHS QUAY LOCAL T2 / HAWARDEN T1 / KING GEORGE ST T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 12.9898 | 13.8699 | 13.7527 | 12.7421 | 11.6636 | 10.294 | 8.8854 | 7.37 | 5.762 | 4.1306 | 2.7654 | -2.2505 | -8.7328 | -13.4581 | -13.3348
| CONWY T1 / DEGANWY T1 / LLANDUDNO JUNCTION T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 14.9731 | 15.528 | 15.3246 | 14.3108 | 13.1329 | 11.6911 | 10.2072 | 8.5389 | 6.6027 | 4.7716 | 3.2425 | -1.7491 | -6.8192 | -6.9664 | -7.0036
| CORWEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.551 | 3.6323 | 3.5591 | 3.202 | 2.8386 | 2.3986 | 1.9712 | 1.5064 | 1.005 | 0.53395 | 0.13881 | -1.2695 | -2.8266 | -3.4787 | -3.6453
| CREWE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.3469 | 2.9122 | -3.1059 | -3.0957 | -3.0957 | -3.1389 | -3.2083 | -3.3043 | -3.4112 | -3.5374 | -3.6283 | -4.6981 | -6.218 | -5.8454 | -5.4707
| CRIGGION RADIO STATION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.1939 | 2.2246 | 2.1976 | 2.098 | 1.9913 | 1.8713 | 1.7592 | 1.6353 | 1.5202 | 1.3876 | 1.2657 | 0.82129 | 0.19327 | 0.033975 | 0.1401
| CROSSFIELDS T1 / CROSSFIELDS T2 / LEVERS CROSSFIELDS T3 / GATEWARTH SEWAGE T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 21.6122 | 22.0566 | 22.1159 | 21.9093 | 21.7566 | 21.5468 | 21.3542 | 21.1777 | 21.0619 | 20.871 | 20.6993 | 19.7916 | 18.3602 | 17.9925 | 18.2953
| CROWTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 3.6531 | 3.8364 | 3.8207 | 3.5988 | 3.355 | 3.0739 | 2.7704 | 2.4423 | 2.1134 | 1.7681 | 1.4629 | 0.38491 | -1.0703 | -1.7857 | -1.875
| CWM DYLI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.6633 | 2.6703 | 2.6453 | 2.5134 | 2.3987 | 2.2449 | 2.1072 | 1.9749 | 1.8038 | 1.6697 | 1.5975 | 1.3959 | 1.2743 | 1.2093 | 1.2675
| DAILY POST & ECHO T1 / DAILY POST & ECHO T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.6286 | 5.1162 | 5.2317 | 5.2386 | 5.2694 | 5.3318 | 5.3516 | 5.3684 | 5.3858 | 5.4066 | 5.4033 | 5.4072 | 5.3329 | 5.3256 | 5.4242
| DARESBURY NPL T1 / DARESBURY NPL T2 / DARESBURY PK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 4.7143 | 4.8218 | 4.7602 | 4.4614 | 4.1498 | 3.7912 | 3.4426 | 3.0812 | 2.7166 | 2.3343 | 1.975 | 0.63459 | -1.2068 | -1.7987 | -1.672
| DAVY WAY T1 / LLAY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.0102 | 2.2653 | 2.2582 | 1.9316 | 1.6549 | 1.3119 | 0.98538 | 0.68485 | 0.41728 | 0.10346 | -0.16629 | -1.4535 | -3.3669 | -4.3688 | -4.0888
| DEESIDE ALUMINIUM T1 / DUNLOP PLASTICS T1 / FIRESTONE T1 / TETRAPAK T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.898 | 3.7382 | 3.8036 | 2.9451 | 2.3594 | 1.6241 | 1.0406 | 0.62513 | 0.48243 | 0.080047 | -0.3278 | -3.1949 | -8.044 | -9.3404 | -8.0072
| DEESIDE IND PK T1 / DEESIDE IND PK 6TH AVE T1 / RAF SEALAND T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 7.2041 | 7.5403 | 7.4749 | 6.9303 | 6.391 | 5.7695 | 5.1878 | 4.6143 | 4.0809 | 3.4577 | 2.8504 | 0.29084 | -3.197 | -3.6487 | -2.8694
| DELAMORE ST T1 / KIRKDALE T1 / WALTON T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 4.6755 | 5.7061 | 5.8519 | 5.5242 | 7.8153 | 7.3915 | 6.9747 | 5.7141 | 5.2832 | 4.7939 | 4.3847 | 2.6659 | 0.48594 | -0.11109 | -0.3606
| DESOTO RD T1 / MERSEY BRIDGE T1 / PITT ST T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 14.4898 | 14.7189 | 14.744 | 14.5801 | 14.4694 | 14.3333 | 14.2203 | 14.1338 | 14.0905 | 14.0154 | 13.9319 | 13.394 | 12.4879 | 12.296 | 12.575
| DIBBINSDALE T1 / PLYMYARD T1 / WIBP HARDKNOTT RD T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 8.7857 | 9.0117 | 8.8507 | 8.1009 | 7.341 | 6.4366 | 5.5116 | 4.5382 | 3.5251 | 2.4596 | 1.4885 | -2.1297 | -6.6262 | -7.5773 | -7.0505
| DINGLE T1 / GRANBY T1 / ST JAMES T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 11.9898 | 12.3045 | 12.3458 | 12.1924 | 12.0808 | 11.9369 | 11.7929 | 11.6729 | 11.5732 | 11.446 | 11.3455 | 10.7911 | 9.9765 | 9.7736 | 9.9146
| DITTON T1 / GAVIN RD T1 / HOUGH GREEN T1 / RTZ T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 12.5204 | 13.1537 | 13.028 | 12.0776 | 11.1167 | 9.9145 | 8.7093 | 7.4896 | 6.2733 | 4.967 | 3.8132 | -1.0114 | -7.5239 | -12.0445 | -11.0446
| DODDS LA T1 / HOLBORN HILL T1 / MAGHULL T1 / MAGHULL T2 / ROBBINS BRIDGE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 13.4898 | 15.3436 | 15.2416 | 13.9456 | 12.3753 | 10.409 | 8.2418 | 5.7508 | 3.0624 | 0.40973 | -1.8284 | -9.7985 | -19.4565 | -26.5301 | -26.751
| DOLGARROG T1 / DOLGARROG T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.051 | 3.0807 | 2.982 | 2.6114 | 2.1929 | 1.725 | 1.2597 | 0.74542 | 0.16323 | -0.37773 | -0.84332 | -2.1868 | -3.8622 | -4.2201 | -3.8779
| DOLGELLAU T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.4082 | 3.4772 | 3.3554 | 2.8779 | 2.3746 | 1.7561 | 1.1467 | 0.47306 | -0.3623 | -1.0775 | -1.6002 | -3.0215 | -4.1815 | -4.0398 | -3.8232
| DUCKINGTON T1 / DUCKINGTON T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.8418 | 4.952 | 4.8483 | 4.4413 | 3.9778 | 3.4635 | 2.8974 | 2.2819 | 1.5886 | 0.92323 | 0.33302 | -1.6283 | -3.82 | -4.0579 | -3.8491
| DUDDON T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 5.3061 | 5.3735 | 5.3594 | 5.2088 | 5.068 | 4.9042 | 4.7344 | 4.5622 | 4.3851 | 4.2065 | 4.05 | 3.4213 | 2.5779 | 2.1828 | 2.161
| DYFFRYN ARDUDWY T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.3265 | 5.2745 | 5.1965 | 4.8487 | 4.4944 | 4.0786 | 3.6762 | 3.2334 | 2.733 | 2.2989 | 1.9801 | 1.0547 | 0.22861 | 0.15203 | 0.035185
| DYSERTH RD T1 / FFORDD LAS T1 / FFORDD LAS T2 / WESTBOURNE AVE T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 10.9082 | 12.5812 | 12.6986 | 12.0571 | 11.3236 | 10.2659 | 9.1458 | 7.8682 | 6.4145 | 5.0733 | 4.1328 | 0.7596 | -2.6039 | -5.4359 | -4.7665
| EDEN VALE T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.0306 | 3.2421 | 3.23 | 3.0151 | 2.7766 | 2.4948 | 2.2023 | 1.8844 | 1.5581 | 1.2257 | 0.92714 | -0.44297 | -3.0702 | -3.3611 | -3.165
| EDERN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 0.84694 | 0.75327 | 1.0497 | 0.43759 | 0.17428 | 0.13091 | -1.7596 | -2.5031 | -3.3965 | -4.181 | -4.8194 | -6.5336 | -8.2308 | -8.4144 | -8.1652
| EDGE HILL T1 / LIVERPOOL UNIVERSITY T1 / LIVERPOOL UNIVERSITY T2 / LIVERPOOL UNIVERSITY T3 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 13.6837 | 14.2017 | 14.1812 | 13.5916 | 13.057 | 12.4274 | 11.8652 | 11.3255 | 10.8621 | 10.2702 | 9.6629 | 7.1854 | 3.0655 | 2.2965 | 3.3049
| EDGE LA (TAPLEY PLACE) T1 / LISTER DV B T3 / MILL LA (WAVERTREE) T1 / PLESSEY (EDGE LA) T1 / STONEYCROFT T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 16.449 | 18.3813 | 18.7143 | 18.5803 | 18.4242 | 18.204 | 17.8619 | 17.4411 | 17.0204 | 16.5144 | 16.1213 | 14.4399 | 12.1058 | 12.3353 | 13.4101
| EGA ELECTRIC T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4 | 4.0578 | 3.9923 | 3.722 | 3.4373 | 3.1141 | 2.7749 | 2.4168 | 2.018 | 1.6187 | 1.2799 | 0.12342 | -1.1933 | -1.3504 | -1.1902
| EGERTON T1 / ROCK FERRY T1 / SHELL TRANMERE T1 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | 5.602 | 6.0732 | 5.9931 | 5.3662 | 4.8955 | 4.3428 | 3.7967 | 3.2565 | 2.7127 | 2.105 | 1.5384 | -0.66294 | -3.999 | -5.0031 | -4.7463
| EGREMONT T1 / LISCARD T1 / POULTON T1 / STONE MANGANESE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 13.2857 | 14.2545 | 14.3957 | 14.0137 | 13.7337 | 13.341 | 12.9742 | 12.6708 | 12.4358 | 12.0998 | 11.824 | 10.2681 | 7.7905 | 7.0748 | 7.643
| ELLESMERE T1 / MMB ELLESMERE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.5918 | 1.7834 | 1.6984 | 1.223 | 0.743 | 0.15436 | -0.42438 | -1.0304 | -1.6758 | -2.3091 | -2.8387 | -4.8782 | -7.519 | -8.9989 | -8.6856
| ELTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 4.7755 | 4.7155 | 4.5795 | 4.2486 | 3.8707 | 3.4397 | 3.0018 | 2.4931 | 1.9453 | 1.4145 | 0.8919 | -0.83748 | -2.8228 | -3.0755 | -2.9849
| ENGINEER PK T1 / PILKINGTONS QUEENSFERRY T1 / QUEENSFERRY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 5.6429 | 6.0843 | 6.0762 | 5.4774 | 5.0121 | 4.4228 | 3.8859 | 3.4149 | 3.0307 | 2.5468 | 2.1173 | -0.079858 | -3.356 | -4.7748 | -4.1201
| ESTUARY COMMERCE PK T1 / LEEWARD DR T1 / LEEWARD DR T2 / SPEKE HALL RD T1 / SPEKE SKY PK T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 21.1633 | 21.4255 | 21.437 | 21.1321 | 20.9118 | 20.6299 | 20.4123 | 20.2454 | 20.1557 | 20.0031 | 19.843 | 18.7959 | 17.1308 | 16.7077 | 17.0675
| EVERTON BROW T1 / GARDNERS ROW T1 / SHEIL PK T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 6.5408 | 7.7118 | 7.9633 | 8.0274 | 8.1152 | 7.9385 | 7.9134 | 7.8631 | 7.8366 | 7.7559 | 7.7264 | 7.3651 | 6.8591 | 6.8712 | 7.1573
| EXPRESS FOODS T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 5.9898 | 6.0376 | 6.0214 | 5.9444 | 5.867 | 5.7795 | 5.6832 | 5.5831 | 5.485 | 5.3759 | 5.2779 | 4.9192 | 4.4567 | 4.3811 | 4.492
| FAIRBOURNE T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 5.2755 | 5.1769 | 5.0271 | 4.628 | 4.2489 | 3.7863 | 3.324 | 2.8178 | 2.2092 | 1.6884 | 1.2605 | 0.058212 | -1.1152 | -1.2893 | -1.1988
| FAZAKERLEY HOSPITAL T1 / JACOBS T1 / JACOBS T2 / SEEDS LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 16.0306 | 17.0243 | 17.1444 | 16.8789 | 16.6324 | 16.3053 | 15.9397 | 15.5605 | 15.2162 | 14.7995 | 14.4142 | 12.7568 | 10.2659 | 9.6765 | 10.0265
| FERODO T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 4.8776 | 4.8958 | 4.7885 | 4.5239 | 4.2205 | 3.8592 | 3.4735 | 3.0546 | 2.5602 | 2.0867 | 1.662 | 0.26829 | -1.4214 | -1.6013 | -1.4516
| FISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.7347 | 4.7972 | 4.7895 | 4.65 | 4.5486 | 4.4268 | 4.3204 | 4.2184 | 4.1408 | 4.0447 | 3.9535 | 3.5264 | 2.8361 | 2.5274 | 2.5258
| FLINT T1 / FLINT T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.949 | 4.2078 | 4.2135 | -0.16327 | -0.41111 | -0.72597 | -1.0396 | -1.3526 | -1.6658 | -2.0039 | -2.3135 | -3.6041 | -5.3566 | -6.0528 | -6.3336
| FODENS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.5 | 2.5828 | 2.5208 | 2.1492 | 1.849 | 1.4748 | 1.1091 | 0.75016 | 0.40167 | 0.024213 | -0.35211 | -1.755 | -3.8688 | -4.934 | -5.2636
| FORD T1 / OXTON T1 / PRENTON LOCAL T1 / SINGLETON AVE T2 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | 12.0204 | 13.2989 | 13.0501 | 11.9446 | 10.7836 | 9.2863 | 7.6852 | 5.835 | 3.8043 | 1.7909 | 0.15601 | -5.9744 | -13.2024 | -19.9421 | -18.6284
| FORDEN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 0.29592 | 1.8416 | 1.9336 | 1.5993 | 1.4805 | 1.2684 | 0.75023 | 0.41433 | 0.035406 | -0.33355 | -0.64189 | -1.6453 | -2.9565 | -3.3019 | -3.1531
| FOUR CROSSES T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.6224 | 1.6781 | 1.6554 | 1.515 | 1.3688 | 1.2087 | 1.0475 | 0.8757 | 0.71171 | 0.53601 | 0.37411 | -0.22266 | -0.97051 | -1.166 | -1.1147
| FRODSHAM LOCAL T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 2.0476 | 2.161 | 1.9112 | 1.2809 | 0.71228 | 0.41984 | -0.76613 | -1.6505 | -2.6423 | -3.5357 | -4.344 | -7.1544 | -10.2599 | -11.4232 | -11.6374
| GADBROOK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.6735 | 3.8137 | 3.7704 | 3.5222 | 3.2573 | 2.9626 | 2.656 | 2.3068 | 1.9361 | 1.5376 | 1.1709 | -0.019425 | -1.862 | -2.4481 | -2.465
| GAERWEN VIEW T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.7653 | 5.7769 | 5.7544 | 5.6158 | 5.495 | 5.336 | 5.1889 | 5.0328 | 4.8697 | 4.6984 | 4.554 | 3.9722 | 3.219 | 3.0673 | 3.0898
| GIGG LA THELWALL T1 / HILLCLIFFE T1 / STOCKTON HEATH T1 / STRETTON IND EST T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 10.2653 | 11.2229 | 11.1441 | 10.111 | 9.0901 | 7.8133 | 6.4825 | 5.096 | 3.6947 | 2.1927 | 0.87493 | -4.1322 | -11.213 | -16.088 | -16.2552
| GILBROOK DOCK T1 / HILL RD T1 / MOBIL OIL (WALLASEY) T1 | 7 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 9.4959 | 10.1533 | 10.211 | 11.7056 | 11.4129 | 11.0367 | 10.6401 | 10.1778 | 9.7531 | 9.3116 | 8.9396 | 7.4088 | 5.7857 | 5.6368 | 5.4678
| GLAN-YR-AFON T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.1735 | 5.2498 | 5.2289 | 5.0787 | 4.9379 | 4.7646 | 4.5959 | 4.4225 | 4.248 | 4.0767 | 3.9375 | 3.4415 | 2.844 | 2.6215 | 2.6571
| GRAIG FAWR T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.2041 | 4.1501 | 3.9381 | 3.3395 | 2.622 | 1.8264 | 0.99785 | 0.096651 | -0.93609 | -1.9336 | -2.827 | -5.6684 | -9.0602 | -9.696 | -9.2728
| GRAVEL T1 / WCB PLASTICS T1 / WHARTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 13.4694 | 13.6663 | 13.6488 | 13.3911 | 13.1401 | 12.8409 | 12.5685 | 12.2809 | 12.0267 | 11.705 | 11.4167 | 10.1403 | 8.2632 | 8.0543 | 8.4474
| GREASBY T1 / SAUGHALL MASSIE T1 / UPTON T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 7.2347 | 7.8035 | 7.666 | 6.8521 | 5.9867 | 4.9214 | 3.7985 | 2.5822 | 1.3212 | 0.044291 | -1.0523 | -5.3759 | -10.775 | -14.5936 | -14.2557
| GREAT SANKEY T1 / PENKETH T1 / WIDNES RD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 9.1837 | 9.4429 | 9.2484 | 8.344 | 7.3636 | 6.187 | 4.9771 | 3.6893 | 2.3533 | 0.99925 | -0.201 | -4.8057 | -10.8394 | -14.9556 | -15.0025
| GREAT SUTTON T1 / LITTLE SUTTON T1 / STRAWBERRY ROUNDABOUT T1 / SUTTON HALL WWB T1 / WHITBY MAIN T2 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 3.42 | 4.7998 | 4.6901 | 3.4785 | 2.1744 | 0.50446 | -1.3018 | -3.2993 | -5.3767 | -7.4856 | -9.3285 | -16.4058 | -25.4427 | -31.5993 | -31.6613
| GREENFIELD T1 / GREENFIELD T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.949 | 4.0461 | 3.9444 | 3.5357 | 3.0881 | 2.5695 | 2.0326 | 1.4676 | 0.86392 | 0.22135 | -0.36888 | -2.5948 | -5.4596 | -5.6704 | -5.2528
| GROSVENOR ST T1 / LINENHALL ST T1 / NORTHGATE TERRACE T1 / STATION VIEW T1 / TOMULAR PLACE T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 8.1429 | 9.5419 | 9.6693 | 9.0377 | 8.6287 | 7.9713 | 7.3364 | 6.7203 | 6.037 | 5.3771 | 4.9367 | 3.0964 | 0.73774 | 0.051508 | 0.74034
| GWERSYLLT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.102 | 2.1442 | 1.9867 | 1.9798 | 1.8001 | 2.9869 | -0.58872 | -1.404 | -2.2955 | -3.1813 | -3.9704 | -6.7002 | -9.7496 | -10.0059 | -9.8938
| HALTON RD T1 / MURDISHAW T1 / PERCIVAL LA T4 / RUNCORN CENTRAL T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 6.4796 | 8.2535 | 8.5174 | 8.2946 | 8.1025 | 7.7952 | 7.3402 | 6.8442 | 6.3096 | 5.7094 | 5.2084 | 3.2693 | 0.22355 | -1.4589 | -1.7033
| HARLECH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.1939 | 5.1275 | 5.0106 | 4.6337 | 4.3055 | 3.8902 | 3.4589 | 2.9841 | 2.4415 | 1.9721 | 1.6056 | 0.49236 | -0.6025 | -0.92582 | -0.98303
| HARRINGTON ST T1 / PARADISE ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 3.4041 | 3.6252 | 3.3165 | 3.0136 | 3.0456 | 2.9511 | 2.7818 | 2.5183 | 2.1993 | 1.9496 | 1.6355 | 0.22884 | -1.6426 | -3.3111 | -3.5731
| HARRINGTON ST T2 / HIGHFIELD ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.4653 | 4.5916 | 4.6036 | 4.4684 | 4.3878 | 4.2827 | 4.2094 | 4.157 | 4.1434 | 4.0969 | 4.0429 | 3.6521 | 2.9757 | 2.7839 | 2.9752
| HARRINGTON ST T3 / LIME ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.4653 | 4.9486 | 5.0478 | 5.1188 | 5.1227 | 5.1817 | 5.2178 | 5.2499 | 5.2825 | 5.2947 | 5.3262 | 5.3286 | 5.28 | 5.3131 | 5.4895
| HARTFORD T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 1.2449 | 1.6474 | 1.6033 | 1.889 | 2.1322 | 0.84289 | -0.79058 | -1.5764 | -2.4374 | -3.2535 | -3.9292 | -6.2066 | -8.8339 | -10.4137 | -10.9518
| HASKAYNE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 5.3776 | 5.4692 | 5.4471 | 5.3013 | 5.1399 | 4.9439 | 4.7433 | 4.5128 | 4.2582 | 4.023 | 3.8035 | 3.0305 | 2.1459 | 2.0581 | 2.0373
| HATHERTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.8265 | 1.8516 | 1.8222 | 1.7088 | 1.6094 | 1.4865 | 1.3763 | 1.2655 | 1.156 | 1.0389 | 0.92435 | 0.50261 | -0.17381 | -0.34822 | -0.20649
| HERONS WAY T1 / LACHE T1 / MBNA T1 / SMFS KINGSMEADOW T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 19.2041 | 19.6553 | 19.6104 | 19.0386 | 18.4647 | 17.7325 | 16.9965 | 16.2224 | 15.4497 | 14.6373 | 13.936 | 11.1372 | 7.5873 | 5.4071 | 5.7565
| HIGHFIELD ST T2 / LIME ST T2 / OLD HAYMARKET T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 10.7505 | 11.0011 | 10.9779 | 10.7549 | 10.6073 | 10.4178 | 10.234 | 10.0493 | 9.8576 | 9.6585 | 9.4217 | 8.4518 | 6.8998 | 6.5903 | 6.9693
| HOLMES CHAPEL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.6939 | 1.7961 | 1.7176 | 1.3085 | 0.89914 | 0.69936 | -0.067808 | -0.55557 | -1.0816 | -1.5933 | -2.0217 | -3.5873 | -5.7194 | -6.9501 | -6.9362
| HOLT LA (WARRINGTON RD) T1 / PRESCOT T1 / RAINHILL LOCAL T1 / WHISTON HOSP T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 10.1735 | 11.6774 | 11.7317 | 11.12 | 10.4547 | 9.5119 | 8.461 | 7.2506 | 5.9697 | 4.6026 | 3.4439 | -1.1 | -6.3351 | -9.7711 | -8.7089
| HOLWAY RD T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.2143 | 3.3271 | 3.2769 | 2.9568 | 2.6647 | 2.3021 | 1.951 | 1.5902 | 1.2141 | 0.85341 | 0.57744 | -0.50949 | -1.7409 | -2.3499 | -2.3092
| HOLYHEAD T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 4.8061 | 4.8366 | 4.7585 | 4.5343 | 4.2481 | 3.9395 | 3.6131 | 3.2331 | 2.7852 | 2.3611 | 1.9589 | 0.82608 | -0.8773 | -1.1117 | -0.87576
| HOLYWELL T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.3469 | 3.4052 | 3.3008 | 2.888 | 2.4091 | 1.8704 | 1.3014 | 0.65661 | -0.0096952 | -0.66275 | -1.2273 | -3.1466 | -5.5266 | -6.2292 | -6.3052
| HOOTON MAIN T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 2.8878 | 2.8793 | 2.7622 | 2.2713 | 1.7665 | 1.1822 | 0.5825 | -0.072616 | -0.71853 | -1.3464 | -1.9209 | -4.1054 | -6.7153 | -7.7836 | -8.0498
| HUNTS CROSS T1 / KENTON RD T1 / WOODEND AVE T1 / WOOLTON T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 13.0102 | 13.8284 | 13.6495 | 12.6132 | 11.5036 | 10.1012 | 8.6259 | 7.0184 | 5.3413 | 3.6203 | 2.126 | -3.7644 | -11.3166 | -16.9679 | -16.2835
| HUYTON HEY RD T1 / WILSON RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 2.9694 | 3.2672 | 3.2205 | 2.7804 | 2.3231 | 1.7454 | 1.1695 | 0.55642 | -0.085735 | -0.7228 | -1.2568 | -3.3402 | -5.9086 | -7.5078 | -7.4282
| IFTON T1 / IFTON T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.9592 | 4.1082 | 4.0378 | 3.6025 | 3.1433 | 2.6007 | 2.0421 | 1.4412 | 0.82389 | 0.20747 | -0.34061 | -2.4522 | -5.1165 | -6.4712 | -6.352
| ILFORDS T1 / KNUTSFORD T1 / MOBBERLEY T1 / RADBROKE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 15.2857 | 15.7468 | 15.6449 | 14.9656 | 14.2285 | 13.3849 | 12.5377 | 11.6132 | 10.6889 | 9.6846 | 8.7531 | 5.2651 | 0.43448 | -0.36598 | 0.22173
| IVY ST (SOUTHPORT) T1 / KENSINGTON RD T1 / MARKET ST T1 / SOUTHPORT T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 14.6633 | 15.2202 | 15.2078 | 14.565 | 13.9364 | 13.2025 | 12.5086 | 11.8063 | 11.1261 | 10.3777 | 9.7097 | 7.032 | 3.1392 | 2.2673 | 2.7482
| IVY ST T1 / LLYSFAEN RD T1 / OLD MILL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 7.9184 | 8.6394 | 8.5328 | 7.7545 | 6.9483 | 5.9013 | 4.8128 | 3.6041 | 2.2723 | 1.0111 | 0.029116 | -3.5215 | -7.4663 | -10.3461 | -10.072
| JOHNSTOWN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.0816 | 1.0993 | 0.92752 | 0.73593 | 0.07496 | -0.54017 | -1.6002 | -2.377 | -3.2223 | -4.0785 | -4.8679 | -7.6101 | -10.9194 | -10.6831 | -10.0828
| KELCO T1 / NEWS INTERNATIONAL T1 / NEWS INTERNATIONAL T2 / PALCO T1 / SOUTHDENE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 12.4286 | 13.0134 | 13.0708 | 22.4884 | 22.0966 | 21.5937 | 21.1738 | 20.8695 | 20.7081 | 20.4031 | 20.1001 | 18.1087 | 14.8867 | 13.8972 | 14.5231
| KINGSLAND 33 T1 / SAFEWAY T1 / WOOLSTON T1 / WOOLSTON T2 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 12.7857 | 14.1303 | 14.301 | 13.96 | 13.6343 | 13.1573 | 12.6145 | 12.0469 | 11.483 | 10.8482 | 10.3048 | 6.5745 | 1.8479 | 1.87 | 2.813
| KINNERTON T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 4.1939 | 4.1197 | 3.9927 | 3.6635 | 3.2476 | 2.818 | 2.3704 | 1.857 | 1.2943 | 0.73849 | 0.20257 | -1.2997 | -3.4215 | -3.8836 | -3.5434
| KIRKBY CENTRAL T1 / NORTHWOOD T1 / TOWER HILL (BANK LA) T1 / WESTVALE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 11.7857 | 13.2484 | 13.2366 | 12.6289 | 11.8892 | 10.8377 | 9.6878 | 8.3785 | 6.9445 | 5.5132 | 4.3427 | -0.39506 | -5.9718 | -10.7183 | -9.2762
| KNOWSLEY T1 / MARLED HEY T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 5.6531 | 5.8885 | 5.9023 | 5.7065 | 5.5426 | 5.3366 | 5.1127 | 4.8835 | 4.6671 | 4.4333 | 4.21 | 3.3322 | 2.1418 | 1.6912 | 1.5387
| KNUTSFORD T2 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.9417 | 2.124 | 2.078 | 1.8076 | 1.5179 | 1.1807 | 0.84313 | 0.42114 | 0.045577 | -0.33876 | -0.6842 | -1.9375 | -3.5891 | -4.113 | -4.049
| LCWW HUNTINGTON T1 / LCWW HUNTINGTON T2 | 7 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.549 | 4.7064 | 4.6952 | 4.4947 | 4.3209 | 4.0973 | 3.8876 | 3.6742 | 3.4677 | 3.2496 | 3.0527 | 2.1881 | 0.91572 | 0.2554 | 0.46684
| LEA GREEN T1 / PILKINGTONS HO T1 / RAVENHEAD RETAIL PK T1 / SOMERFIELD DISTRIBUTION T1 | 11 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 7.1327 | 8.1623 | 8.2944 | 8.012 | 7.7663 | 7.4062 | 7.0023 | 6.5736 | 6.1521 | 5.6524 | 5.2233 | 3.511 | 0.86946 | -0.38889 | -0.62467
| LEGACY LOCAL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.2041 | 5.4018 | 5.401 | 5.3041 | 5.1585 | 4.9699 | 4.756 | 4.4994 | 4.2226 | 3.9629 | 3.7372 | 3.0199 | 2.3777 | 2.3924 | 2.4455
| LEIGHTON HOSP T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.9796 | 4.2742 | 4.2948 | 4.2551 | 4.1751 | 4.0965 | 3.9866 | 3.8464 | 3.6976 | 3.5643 | 3.4655 | 2.913 | 1.9983 | 1.9159 | 2.2283
| LIVERPOOL RD 33 T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 6.9592 | 7.1109 | 7.041 | 6.7472 | 6.4374 | 6.0445 | 5.6527 | 5.2198 | 4.7204 | 4.2511 | 3.8739 | 2.5711 | 1.2079 | 1.3261 | 1.6187
| LLAINGOCH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 4.3061 | 4.4235 | 4.2558 | 3.8948 | 3.406 | 2.8126 | 2.179 | 1.4329 | 0.53272 | -0.33467 | -1.0943 | -3.3103 | -5.566 | -5.1762 | -4.6063
| LLANARMON T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 5.9286 | 5.9924 | 5.9777 | 5.8978 | 5.7964 | 5.6869 | 5.564 | 5.4371 | 5.3066 | 5.1709 | 5.0573 | 4.6446 | 4.0093 | 3.5959 | 3.5728
| LLANBEDROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.9694 | 1.9731 | 1.9097 | 1.6592 | 1.3948 | 1.0787 | 0.77928 | 0.43718 | 0.047111 | -0.29365 | -0.57243 | -1.3894 | -2.1758 | -2.2183 | -2.1963
| LLANBERIS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 1.4592 | 1.5969 | 1.5601 | 1.3019 | 1.0456 | 0.71361 | 0.39187 | 0.040915 | -0.35943 | -0.73544 | -1.0137 | -1.9272 | -2.8554 | -2.8818 | -2.6774
| LLANDDEUSANT T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.7653 | 3.8774 | 3.7941 | 3.5304 | 3.2008 | 2.8369 | 2.4349 | 1.9679 | 1.431 | 0.91365 | 0.45224 | -0.90402 | -2.4406 | -2.6834 | -2.315
| LLANDDU QUARRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 0.52041 | 0.69751 | 0.70447 | 0.56024 | 0.41437 | 0.23592 | 0.051503 | -0.14483 | -0.33794 | -0.53761 | -0.7249 | -1.4359 | -2.4314 | -2.901 | -2.8524
| LLANDEGFAN T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.0204 | 5.1065 | 5.0737 | 4.9141 | 4.7121 | 4.4855 | 4.2356 | 3.9547 | 3.6545 | 3.3689 | 3.1145 | 2.1975 | 0.95407 | 0.10406 | 0.16779
| LLANDRINIO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.5353 | 2.5496 | 2.4931 | 2.4125 | 2.3248 | 2.0628 | 1.4954 | 1.2056 | 0.90242 | 0.60556 | 0.33896 | -0.62359 | -1.9631 | -2.4635 | -2.4889
| LLANDUDNO T1 / LLANDUDNO T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.8878 | 4.2896 | 4.266 | 4.0092 | 3.7033 | 3.3406 | 2.9535 | 2.5086 | 1.9766 | 1.4622 | 1.0428 | -0.12705 | -1.8434 | -2.2695 | -2.0268
| LLANDYFRYDOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.1531 | 5.2052 | 5.1601 | 4.9381 | 4.7199 | 4.44 | 4.1634 | 3.8769 | 3.5399 | 3.2449 | 3.0014 | 2.2426 | 1.2985 | 0.76457 | 0.7131
| LLANDYRNOG T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 1.9184 | 2.0786 | 2.0768 | 1.9528 | 1.8237 | 1.6687 | 1.5006 | 1.3313 | 1.1554 | 0.9694 | 0.81701 | 0.20731 | -0.7181 | -1.2561 | -1.1813
| LLANFAELOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 1.2857 | 1.3553 | 1.3318 | 1.1978 | 1.0609 | 0.89085 | 0.72188 | 0.55379 | 0.37814 | 0.20413 | 0.062721 | -0.46681 | -1.1198 | -1.143 | -0.80796
| LLANFAIR CAEREINION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.4388 | 2.539 | 2.4178 | 1.996 | 1.5164 | 0.97591 | 0.41737 | -0.20657 | -0.89775 | -1.5467 | -2.0843 | -3.7624 | -5.6874 | -6.2042 | -5.9999
| LLANFAIR PG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.3571 | 3.4995 | 3.4128 | 3.0821 | 2.7009 | 2.2446 | 1.7696 | 1.2348 | 0.59951 | -0.00039513 | -0.50036 | -1.979 | -3.255 | -3.154 | -2.7629
| LLANFAIRFECHAN T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 5.4082 | 5.4359 | 5.3761 | 5.1211 | 4.8611 | 4.5302 | 4.222 | 3.8849 | 3.471 | 3.1126 | 2.8469 | 2.0082 | 1.2436 | 0.74037 | 0.8075
| LLANFROTHEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.4082 | 5.3748 | 5.2937 | 4.983 | 4.6445 | 4.2543 | 3.8641 | 3.43 | 2.9435 | 2.5086 | 2.1537 | 0.99691 | -0.18311 | -0.23634 | -0.26641
| LLANFWROG T1 / RUTHIN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 5.7959 | 6.2057 | 6.1404 | 5.6203 | 5.0562 | 4.3797 | 3.672 | 2.9134 | 1.8985 | 1.0793 | 0.13811 | -3.1119 | -7.2152 | -7.4563 | -7.0457
| LLANFYLLIN T1 / LLANFYLLIN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.5449 | 2.7899 | 4.9406 | 4.4972 | 4.0596 | 3.4994 | 2.9394 | 2.3393 | 1.6199 | 0.99457 | 0.56489 | -0.82288 | -2.1774 | -2.8934 | -2.9747
| LLANGAFFO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.8061 | 3.8838 | 3.8441 | 3.62 | 3.3843 | 3.0873 | 2.7997 | 2.4744 | 2.1555 | 1.8198 | 1.5247 | 0.39466 | -1.1771 | -2.1465 | -1.9803
| LLANGEFNI IND EST T1 / LLANGEFNI IND EST T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5204 | 3.7304 | 3.7426 | 3.5281 | 3.3645 | 3.1633 | 2.9801 | 2.8347 | 2.741 | 2.5896 | 2.4409 | 1.6093 | 0.26814 | -0.15208 | 0.12672
| LLANGEFNI T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5612 | 3.6588 | 3.6039 | 3.2994 | 2.9884 | 2.6009 | 2.2107 | 1.7974 | 1.3634 | 0.9289 | 0.56452 | -0.80936 | -2.3244 | -2.6237 | -2.5722
| LLANGOLLEN T1 / LLANGOLLEN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.0918 | 5.2705 | 5.2189 | 4.8456 | 4.4551 | 3.9704 | 3.477 | 2.9529 | 2.3551 | 1.804 | 1.406 | 0.034219 | -1.4702 | -2.3859 | -2.163
| LLANIDLOES T1 / LLANIDLOES T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.3729 | 1.5099 | 1.3895 | 0.81539 | 0.49078 | 0.099735 | -1.2418 | -2.0356 | -3.0609 | -3.9298 | -4.5482 | -6.3167 | -7.8708 | -7.7971 | -7.9925
| LLANILAR T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 0.78163 | 0.79526 | 0.72993 | 0.50376 | 0.52764 | 0.60092 | -0.38805 | -0.73758 | -1.1141 | -1.48 | -1.8027 | -2.8126 | -3.9781 | -4.2441 | -4.1522
| LLANRWST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.9592 | 4.1514 | 4.1244 | 3.8808 | 3.629 | 3.3042 | 2.9717 | 2.6054 | 2.1816 | 1.8054 | 1.5309 | 0.61493 | -0.28919 | -0.82798 | -0.62737
| LLANSANNAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.7449 | 4.7652 | 4.6874 | 4.3878 | 4.0602 | 3.6828 | 3.2969 | 2.8837 | 2.3853 | 1.9573 | 1.6351 | 0.8246 | -0.0089489 | -0.1831 | 0.0086211
| LLANSILIN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.9898 | 4.079 | 4.0005 | 3.6931 | 3.3331 | 2.9192 | 2.5003 | 2.0333 | 1.4966 | 1.0106 | 0.60859 | -0.51387 | -1.7837 | -2.1356 | -2.0105
| LLYNCLYS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.3265 | 3.2743 | 3.148 | 2.7846 | 2.3294 | 1.847 | 1.3664 | 0.81259 | 0.21617 | -0.37455 | -0.92826 | -2.494 | -4.8294 | -5.377 | -5.0731
| LORD ST T1 / MARSHSIDE T1 / MULLARDS BALMORAL DV T1 / SOUTHPORT T2 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 11.949 | 13.0816 | 12.7752 | 11.282 | 9.4844 | 7.2756 | 4.8902 | 2.1342 | -0.81218 | -3.6641 | -6.0974 | -15.0044 | -25.1868 | -32.3126 | -32.4963
| LOSTOCK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.1531 | 3.2531 | 3.1599 | 2.8325 | 2.4486 | 2.0187 | 1.5519 | 1.0502 | 0.50457 | -0.043676 | -0.54078 | -2.2989 | -4.6302 | -5.4385 | -5.3712
| LOSTOCK TRIANGLE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.6327 | 4.6082 | 4.5319 | 4.3752 | 4.1352 | 3.8956 | 3.6681 | 3.3804 | 3.0679 | 2.7248 | 2.3956 | 1.3993 | -0.32277 | -0.722 | -0.43269
| LOWER BEBINGTON T1 / NEW FERRY T1 / SPITAL T1 / UNILEVER RESEARCH T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 15.2245 | 15.578 | 15.1898 | 13.8557 | 12.4759 | 10.7739 | 8.9894 | 7.0039 | 4.8627 | 2.7585 | 0.91861 | -5.8348 | -13.37 | -18.0547 | -17.5643
| LUGSDALE T1 / PILK SULLIVAN T1 / PILK SULLIVAN T2 / USAC T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 20.398 | 20.7082 | 20.7265 | 20.3428 | 20.1276 | 19.8324 | 19.5837 | 19.4223 | 19.3414 | 19.1968 | 19.062 | 18.0888 | 16.5826 | 16.3732 | 16.9064
| LYMM T1 / WHITELEGGS LA T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 0.94898 | 2.7775 | 2.6139 | 2.5366 | 1.0844 | 0.38418 | -0.97863 | -2.183 | -3.5291 | -4.8628 | -6.0591 | -9.9245 | -14.5589 | -14.6521 | -14.307
| MACHYNLLETH T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 1.4082 | 1.4051 | 1.3011 | 0.97099 | 0.60457 | 0.16304 | -0.28939 | -0.80448 | -1.4345 | -1.9901 | -2.4282 | -3.7829 | -5.0855 | -4.6963 | -4.328
| MACHYNLLETH T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.3773 | 2.385 | 2.3138 | 2.0402 | 1.7459 | 1.3952 | 1.0445 | 0.6555 | 0.20301 | -0.20378 | -0.53035 | -1.5084 | -2.5129 | -2.6476 | -2.5482
| MAELOR CREAMERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.0612 | 4.22 | 4.2276 | 4.1165 | 4.0279 | 3.9283 | 3.8225 | 3.7418 | 3.6648 | 3.5662 | 3.4836 | 3.0745 | 2.4513 | 2.2973 | 2.4667
| MAENTWROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.9082 | 5.8864 | 5.8215 | 5.6247 | 5.4343 | 5.2039 | 4.9586 | 4.7019 | 4.4183 | 4.1564 | 3.9286 | 3.148 | 2.3173 | 2.218 | 2.1803
| MAES-Y-CLAWDD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.8163 | 2.966 | 2.9386 | 2.7159 | 2.4877 | 2.2458 | 2.0123 | 1.5743 | 1.1152 | 0.60698 | 0.071728 | -1.7207 | -4.3813 | -5.0384 | -4.8671
| MANOD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.8571 | 2.806 | 2.7449 | 2.5509 | 2.3519 | 2.1066 | 1.8659 | 1.605 | 1.2955 | 1.0176 | 0.79668 | 0.24017 | -0.36102 | -0.31846 | -0.20409
| MANOR PK T1 / NORTON CHAINS T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 0.84694 | 2.2613 | 1.7145 | 0.85592 | 0.46004 | 0.019104 | -0.54956 | -1.2445 | -2.0393 | -2.6413 | -3.4155 | -6.8693 | -11.5204 | -14.9565 | -15.6045
| MDHB EGERTON DOCK T1 / MDHB EGERTON DOCK T2 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 3.5485 | 3.9529 | 3.8463 | 3.2748 | 3.5325 | 2.7952 | 2.0398 | 1.173 | 0.2495 | -0.69118 | -1.5229 | -4.6176 | -8.6538 | -10.9099 | -10.4576
| MERE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.7653 | 2.739 | 2.5565 | 1.9574 | 2.1247 | 2.6859 | -0.31938 | -1.2186 | -2.1818 | -3.1046 | -3.9009 | -6.6686 | -9.7826 | -10.4533 | -10.9009
| MERES EDGE T1 / MERES EDGE T2 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 5.4694 | 5.496 | 5.3421 | 4.8738 | 4.3145 | 3.6676 | 3.0078 | 2.2609 | 1.3994 | 0.58196 | -0.13925 | -2.4764 | -5.1953 | -5.5807 | -5.4371
| MIDDLEWICH T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.7653 | 3.7444 | 3.7998 | 5.0976 | 4.5143 | 4.05 | 3.5996 | 2.4354 | 1.9132 | 1.4123 | 0.98624 | -0.60121 | -2.4267 | -3.334 | -3.266
| MIDPOINT POCHIN WAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 5.7755 | 5.8271 | 5.8198 | 5.7591 | 5.7153 | 5.6554 | 5.6008 | 5.5568 | 5.5262 | 5.4775 | 5.4344 | 5.2036 | 4.8091 | 4.6803 | 4.7415
| MILFORD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.9388 | 3.1109 | 3.0563 | 2.7611 | 2.4508 | 2.0771 | 1.7217 | 1.3021 | 0.83207 | 0.39645 | 0.016126 | -1.1817 | -2.7972 | -3.1355 | -3.045
| MINFFORDD T1 / PARC BRYN CEGIN T1 / PARC BRYN CEGIN T2 | 11 | BANGOR GT2 / CAERNARFON GT2 | 16.3265 | 16.4272 | 16.3714 | 16.1118 | 15.8373 | 15.479 | 15.1153 | 14.7495 | 14.3265 | 13.9223 | 13.594 | 12.316 | 10.9662 | 10.201 | 10.6465
| MOCHDRE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.7857 | 3.9192 | 3.9121 | 3.7598 | 3.6316 | 3.4729 | 3.329 | 3.2005 | 3.0789 | 2.934 | 2.8073 | 2.2119 | 1.3998 | 1.1667 | 1.1813
| MONA T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.7347 | 5.7474 | 5.7149 | 5.5689 | 5.4141 | 5.2315 | 5.0401 | 4.8401 | 4.6256 | 4.4054 | 4.2269 | 3.5383 | 2.6405 | 2.3069 | 2.2666
| MONSANTO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.9898 | 5.9721 | 5.8934 | 5.6381 | 5.3869 | 5.0661 | 4.76 | 4.415 | 3.9946 | 3.643 | 3.3673 | 2.4646 | 1.6199 | 1.2007 | 1.0921
| MORDA T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 4.102 | 4.0768 | 3.9461 | 3.6105 | 3.1497 | 2.6493 | 2.1226 | 1.5064 | 0.83057 | 0.14667 | -0.49752 | -2.4734 | -4.553 | -4.5787 | -4.1863
| MORGANITE CERAMICS T1 / PLYMYARD T2 / VAUXHALL NORTH RD T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 13.102 | 13.1901 | 13.0364 | 12.4282 | 11.779 | 10.9936 | 10.1934 | 9.3093 | 8.394 | 7.4519 | 6.5798 | 3.2635 | -0.70197 | -1.4811 | -1.4263
| MORRISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.0816 | 2.2375 | 2.2175 | 1.973 | 1.7515 | 1.493 | 1.2526 | 1.0072 | 0.7995 | 0.56807 | 0.33837 | -0.63258 | -1.9311 | -2.2434 | -2.1257
| NANTWICH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.8163 | 1.9205 | 1.7869 | 1.3665 | 1.5895 | 2.0977 | 0.099692 | -0.4199 | -0.98302 | -1.5339 | -2.086 | -3.8802 | -6.6346 | -7.7479 | -7.7862
| NANT-Y-GAMAR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 2.6531 | 2.8058 | 2.7511 | 2.4036 | 2.0555 | 1.7427 | 1.2137 | 0.78055 | 0.32906 | -0.1188 | -0.51188 | -2.0095 | -3.9222 | -5.051 | -5.0538
| NEVILL ST T1 / OCEAN PLAZA T1 / YORK RD T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 9.551 | 9.8522 | 9.8542 | 9.3879 | 9.0373 | 8.5836 | 8.1941 | 7.8561 | 7.5773 | 7.249 | 6.9688 | 5.543 | 3.4988 | 2.8874 | 3.1496
| NEW BRIGHTON T1 / SEAVIEW RD T2 / WALLASEY T1 / WALLASEY VILLAGE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 15.449 | 16.6247 | 16.6192 | 15.7944 | 14.9738 | 13.9188 | 12.7891 | 11.5246 | 10.0829 | 8.7341 | 7.7128 | 4.5741 | 0.89127 | -1.0162 | -2.2225
| NEWHALL T1 / NEWHALL T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 6 | 6.1099 | 6.1081 | 5.9419 | 5.8132 | 5.6635 | 5.5139 | 5.3821 | 5.2731 | 5.1359 | 5.0104 | 4.3832 | 3.4164 | 3.1091 | 3.2731
| NORTH WALES PAPER T1 / NORTH WALES PAPER T2 / WOODFIELD AVE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 7.398 | 7.8353 | 7.8084 | 7.2842 | 6.8475 | 6.292 | 5.7668 | 5.277 | 4.8425 | 4.3249 | 3.8764 | 1.7028 | -1.4503 | -3.2309 | -2.5723
| NORTH WEST WATER CAMPUS T1 / NORTH WEST WATER CAMPUS T2 / OMEGA T1 / OMEGA T2 / ORION BOULEVARD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 24.8776 | 25.8151 | 25.9286 | 25.5969 | 25.3581 | 25.0204 | 24.6744 | 24.1664 | 23.9043 | 23.5508 | 23.2583 | 21.7783 | 19.7665 | 19.5786 | 20.3852
| OPTICAL FIBRES T1 / SHOTWICK T1 / WALBRO T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 7.2041 | 7.5749 | 7.6106 | 7.1862 | 6.9081 | 6.5655 | 6.2893 | 6.121 | 6.0688 | 5.8942 | 5.726 | 4.4297 | 2.1841 | 1.5926 | 2.2287
| ORB CL T1 / STONEBRIDGE LA T1 / STONEBRIDGE LA T2 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 10.8163 | 11.1139 | 11.1099 | 10.7114 | 10.3979 | 10.0024 | 9.638 | 9.3072 | 9.0369 | 8.7041 | 8.3926 | 6.8645 | 4.5629 | 3.7282 | 3.7734
| ORFORD T1 / PADGATE T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 1.051 | 4.8144 | 4.6841 | 2.4431 | 1.2417 | -0.34638 | -2.1365 | -4.2834 | -6.7848 | -9.0396 | -11.2031 | -19.1524 | -28.0754 | -35.7664 | -35.6642
| OTIS ELEVATOR T1 / ST IVEL FOODS T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 5.0306 | 5.1721 | 5.1895 | 5.0198 | 4.9123 | 4.7789 | 4.6699 | 4.5992 | 4.5803 | 4.5136 | 4.4471 | 3.9353 | 3.0862 | 2.8806 | 3.1437
| OVERTON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.8571 | 3.8593 | 3.7382 | 3.1674 | 2.6607 | 2.0051 | 1.3935 | 0.74037 | -0.080392 | -0.74086 | -1.1195 | -2.0209 | -2.3955 | -2.2771 | -2.2435
| PANDY T1 / PANDY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 1.7143 | 2.3587 | 2.3953 | 2.0748 | 1.7584 | 1.3356 | 0.8641 | 0.32734 | -0.26087 | -0.84454 | -1.3919 | -3.3162 | -5.9638 | -7.1337 | -7.7197
| PARC CYBI T1 / PARC CYBI T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 7.0816 | 7.108 | 7.0538 | 6.8172 | 6.5872 | 6.3222 | 6.072 | 5.8142 | 5.5295 | 5.2766 | 5.0573 | 4.3097 | 3.3472 | 3.0594 | 3.058
| PARC MENAI T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 5.9898 | 5.9998 | 5.9537 | 5.8405 | 5.7037 | 5.548 | 5.3779 | 5.2007 | 4.9889 | 4.778 | 4.5725 | 3.9979 | 3.2203 | 3.1735 | 3.3702
| PEBLIC MILLS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 6.398 | 6.356 | 6.3011 | 6.1705 | 5.8838 | 5.6941 | 5.4992 | 5.0946 | 4.5975 | 4.0855 | 3.5914 | 2.2796 | 0.36165 | -0.10574 | 0.13239
| PENMAENMAWR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 5.1429 | 5.1374 | 5.0346 | 4.6674 | 4.2887 | 3.824 | 3.3648 | 2.8438 | 2.2144 | 1.6645 | 1.2198 | -0.12288 | -1.4466 | -1.3679 | -1.2781
| PENTRAETH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.0612 | 3.1907 | 3.1394 | 2.7643 | 2.4093 | 1.962 | 1.5374 | 1.0706 | 0.57846 | 0.12211 | -0.23482 | -1.5123 | -3.0564 | -3.87 | -4.0896
| PEN-Y-GROES T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 2.3122 | 2.3007 | 2.2235 | 1.8931 | 1.5482 | 1.139 | 0.73486 | 0.31386 | -0.18145 | -0.6246 | -0.95127 | -2.0363 | -3.5427 | -4.2332 | -4.0977
| PILKINGTONS T1 / PILKINGTONS T2 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 6.4592 | 6.6158 | 6.6169 | 6.4647 | 6.3261 | 6.1457 | 5.9594 | 5.777 | 5.5988 | 5.3974 | 5.2523 | 4.6415 | 3.7698 | 3.2906 | 3.4281
| POINT OF AYR COLLIERY T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 2.2755 | 2.3799 | 2.3202 | 2.0064 | 1.6728 | 1.2787 | 0.8944 | 0.51008 | 0.076523 | -0.34807 | -0.71547 | -2.0163 | -3.6288 | -3.8724 | -3.5674
| PORTHMADOG T1 / PORTHMADOG T2 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.6633 | 5.7504 | 5.6373 | 5.1904 | 4.6986 | 4.0936 | 3.4852 | 2.8139 | 2.0172 | 1.2988 | 0.73756 | -1.0124 | -2.8466 | -2.5663 | -2.3372
| PREES T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 2.1633 | 2.5128 | 2.5035 | 2.3064 | 2.04 | 1.7325 | 1.3753 | 0.98269 | 0.51863 | 0.090588 | -0.28929 | -1.3954 | -2.7481 | -3.01 | -2.7271
| PRIMROSE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.8265 | 4.8937 | 4.8823 | 4.7361 | 4.6048 | 4.4457 | 4.3015 | 4.1552 | 4.0184 | 3.8772 | 3.7379 | 3.1827 | 2.433 | 2.2022 | 2.1733
| PWLLHELI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.8673 | 4.0295 | 3.9954 | 3.7345 | 3.4737 | 3.1349 | 2.7978 | 2.4387 | 2.0384 | 1.6713 | 1.4014 | 0.44895 | -0.46288 | -1.0347 | -0.91243
| RADWAY GREEN T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.3469 | 1.5352 | 1.4754 | 1.0728 | 1.3414 | 1.5869 | -0.26602 | -0.75672 | -1.2417 | -1.7422 | -2.1811 | -3.872 | -6.1368 | -7.5535 | -7.6336
| RAVEN SQUARE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.0102 | 1.2409 | 1.1853 | 0.77853 | 0.39025 | 0.44932 | -0.60527 | -1.1274 | -1.708 | -2.2619 | -2.7494 | -4.5619 | -6.5183 | -6.6931 | -6.5687
| REFORM ST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 2.7551 | 3.0084 | 2.9608 | 2.6967 | 2.5122 | 2.2578 | 2.0011 | 1.7096 | 1.3542 | 1.0324 | 0.79028 | 0.033019 | -0.90688 | -1.3478 | -1.2063
| RHM FOODS LTD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 6.2347 | 6.2716 | 6.2738 | 6.2262 | 6.1993 | 6.1648 | 6.1383 | 6.1181 | 6.1073 | 6.092 | 6.0766 | 5.9448 | 5.7317 | 5.6721 | 5.7279
| RHOSLAN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.2143 | 4.2126 | 4.0861 | 3.6609 | 3.1593 | 2.5926 | 2.0136 | 1.3341 | 0.57327 | -0.11898 | -0.71924 | -2.4491 | -4.0631 | -4.121 | -4.0095
| RHUDDLAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.2857 | 3.5643 | 3.5242 | 3.3018 | 2.9986 | 2.6454 | 2.2563 | 1.8054 | 1.2917 | 0.79285 | 0.36694 | -0.95062 | -2.3272 | -2.3058 | -2.1652
| RHYDLYDAN T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.9286 | 2.9241 | 2.8684 | 2.7302 | 2.5342 | 2.3302 | 2.1096 | 1.8608 | 1.5622 | 1.297 | 1.0805 | 0.51053 | -0.19642 | -0.31142 | -0.24846
| RHYD-Y-FOEL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 4.9184 | 4.8447 | 4.7315 | 4.4105 | 4.0448 | 3.6303 | 3.2215 | 2.6963 | 2.1715 | 1.6874 | 1.2697 | 0.11902 | -1.225 | -1.3633 | -1.0528
| RINGWAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | -0.046939 | 6.5729 | 6.5244 | 6.3153 | 6.0249 | 5.7081 | 5.3571 | 4.9399 | 4.4828 | 4.0491 | 3.6504 | 2.5328 | 1.3751 | 1.3521 | 1.3865
| RIVALS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.6224 | 2.5546 | 2.4613 | 2.2463 | 3.1868 | 2.8991 | 2.6142 | 2.2853 | 1.8785 | 1.5326 | 1.2218 | 0.47472 | -0.33947 | -0.41432 | -0.21909
| ROLLS ROYCE T1 / ROLLS ROYCE T2 / ROLLS ROYCE T3 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.1224 | 4.0453 | 4.1504 | 3.9611 | 3.8229 | 3.6197 | 3.3806 | 2.9285 | 2.4132 | 1.852 | 1.2798 | -0.71206 | -3.8407 | -4.8538 | -4.5667
| ROSSETT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.2245 | 3.4955 | 2.5606 | 1.7408 | 0.79789 | 0.047835 | -0.89748 | -2.0888 | -3.5626 | -4.6144 | -5.9054 | -10.212 | -15.6556 | -19.1978 | -20.0551
| ROYAL INSURANCE (NEW QUAY) T1 / ROYAL INSURANCE (NEW QUAY) T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 8.2612 | 8.1596 | 8.0576 | 7.9146 | 7.7214 | 7.4994 | 7.2599 | 6.9429 | 6.5667 | 6.1928 | 5.8102 | 4.8733 | 3.2564 | 3.0462 | 3.3538
| RUABON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.1837 | 3.3884 | 3.2887 | 2.8534 | 2.4235 | 1.8799 | 1.3298 | 0.74812 | 0.14916 | -0.4548 | -0.97585 | -3.102 | -5.7637 | -7.6946 | -7.3379
| SALTNEY T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.9388 | 4.9588 | 4.9197 | 4.7642 | 4.5994 | 4.4138 | 4.2303 | 4.0305 | 3.8121 | 3.5863 | 3.3817 | 2.6521 | 1.6198 | 1.4752 | 1.7258
| SANDBACH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | -0.16327 | 1.1929 | 9.4939 | 9.9287 | 6.8251 | 6.3025 | 5.7871 | 5.2506 | 4.6923 | 4.1414 | 3.6756 | 1.8747 | -0.42674 | -1.7919 | -1.7367
| SHAWBURY T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.4601 | 1.5243 | 1.4446 | 1.096 | 0.71418 | 0.30816 | -0.099467 | -0.70453 | -1.3689 | -2.0599 | -2.7407 | -5.0207 | -7.9945 | -8.8926 | -8.6977
| SMALLWOOD T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.7653 | 1.7309 | 1.426 | 1.8887 | 1.7195 | 0.69786 | -1.307 | -2.2398 | -3.2843 | -4.2345 | -5.185 | -8.3074 | -11.954 | -13.065 | -12.8291
| SNOWHILL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.9184 | 2.0547 | 1.9583 | 1.5725 | 1.1731 | 0.70773 | 0.25986 | -0.24514 | -0.81155 | -1.3779 | -1.8757 | -3.3996 | -5.7026 | -6.4695 | -6.3611
| ST ASAPH BUSINESS PK T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 2.9997 | 2.8487 | 2.6506 | 2.2166 | 1.899 | 1.435 | 0.97076 | 0.3785 | -0.54241 | -1.3424 | -2.0008 | -4.0637 | -5.657 | -6.4632 | -4.9553
| ST HELENS RD T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 3.2245 | 3.3578 | 3.3204 | 3.0579 | 2.7989 | 2.466 | 2.1497 | 1.8146 | 1.4505 | 1.0877 | 0.80699 | -0.2886 | -1.4836 | -2.1095 | -1.7211
| STAPELEY T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4592 | 2.5021 | 2.2249 | 1.6816 | 1.3712 | 0.93874 | 0.44282 | -0.14633 | -0.8047 | -1.3383 | -1.9483 | -4.2837 | -7.2922 | -9.4997 | -9.9496
| TACO PLASTICS T1 / TACO PLASTICS T2 / UNITED PERIPHERALS T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 8.9082 | 9.155 | 9.1149 | 8.4651 | 8.1109 | 7.6125 | 7.1637 | 6.8487 | 6.59 | 6.2703 | 6.0177 | 4.7603 | 3.059 | 3.3227 | 4.2331
| TARPORLEY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.2959 | 3.4298 | 3.3601 | 3.0451 | 2.674 | 2.2487 | 1.8041 | 1.2899 | 0.74854 | 0.22462 | -0.2436 | -1.8002 | -3.7229 | -4.1279 | -4.1304
| TARVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 1.5204 | 1.7747 | 1.7215 | 1.3995 | 1.3597 | 1.8868 | -0.21384 | -0.84537 | -1.4991 | -2.1609 | -2.7351 | -4.8094 | -7.5998 | -9.2583 | -9.3192
| TRYWERYN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.2755 | 2.3485 | 2.3403 | 2.2266 | 2.1372 | 2.0122 | 1.908 | 1.7907 | 1.656 | 1.5377 | 1.4852 | 1.3078 | 1.1709 | 1.1179 | 1.2029
| TWYFORDS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.4388 | 4.609 | 4.5818 | 4.4122 | 4.2412 | 4.0202 | 3.7974 | 3.5595 | 3.3042 | 3.0416 | 2.8127 | 1.9326 | 0.73628 | -0.1725 | -0.11072
| TYWYN T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 3.2041 | 3.2283 | 3.0602 | 2.4816 | 2.0461 | 1.4087 | 0.79713 | 0.12453 | -0.68861 | -1.3862 | -1.8991 | -3.6193 | -5.2139 | -6.2736 | -6.4425
| WAENFAWR T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 4.3571 | 4.4174 | 4.3323 | 3.9834 | 3.5794 | 3.1025 | 2.6234 | 2.0663 | 1.4691 | 0.91796 | 0.44953 | -1.0857 | -2.7595 | -2.9988 | -3.0767
| WELSHPOOL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.5204 | 3.6294 | 3.5923 | 3.3747 | 3.141 | 2.8917 | 2.6151 | 2.3418 | 2.0627 | 1.7654 | 1.4971 | 0.5657 | -0.71365 | -1.1479 | -0.96057
| WEM EAST T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 4.5612 | 4.6615 | 4.6392 | 4.4532 | 4.2647 | 4.0315 | 3.8063 | 3.577 | 2.9757 | 2.6962 | 2.1748 | 0.5326 | -1.1639 | -0.59175 | -0.12939
| WEM T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 2.6939 | 2.8243 | 2.7372 | 2.4219 | 2.0184 | 1.5808 | 1.1144 | 0.56754 | -0.034279 | -0.63019 | -1.181 | -2.8928 | -5.0001 | -5.4971 | -5.1298
| WERVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.2857 | 4.291 | 4.1869 | 3.8851 | 3.5006 | 3.0854 | 2.6472 | 2.1648 | 1.5909 | 1.0412 | 0.55089 | -0.85192 | -2.888 | -3.4176 | -3.3419
| WEST FELTON T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.0204 | 1.1047 | 1.0862 | 0.93296 | 0.76476 | 0.58177 | 0.38649 | 0.18934 | -0.01921 | -0.23212 | -0.43252 | -1.113 | -2.0311 | -2.2888 | -2.081
| WESTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.8673 | 3.1208 | 3.0254 | 2.5854 | 2.1076 | 1.5454 | 0.94636 | 0.29662 | -0.39211 | -1.0727 | -1.6846 | -3.9496 | -7.0321 | -8.9715 | -8.8137
| WHEELOCK T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4286 | 2.644 | 2.5833 | 2.2223 | 1.8111 | 1.3282 | 0.80764 | 0.22598 | -0.40855 | -1.0254 | -1.5659 | -3.532 | -5.9487 | -7.3314 | -7.4103
| WHITCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 5.8571 | 6.1064 | 6.0872 | 5.808 | 5.504 | 5.1406 | 4.7417 | 4.3237 | 3.8841 | 3.4504 | 3.0718 | 1.6602 | -0.24605 | -1.2696 | -1.2598
| WIMPEYS PANT QUARRY T1 / WIMPEYS PANT QUARRY T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 1.0673 | 6.093 | 6.0655 | 5.8716 | 5.6339 | 5.3735 | 5.0831 | 4.7655 | 4.4365 | 4.0987 | 3.8075 | 2.7572 | 1.2854 | 0.77375 | 0.76172
| WINCHAM T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 5.1327 | 5.1718 | 5.1429 | 5.0157 | 4.881 | 4.7287 | 4.5774 | 4.4176 | 4.266 | 4.0904 | 3.9306 | 3.3222 | 2.5079 | 2.2887 | 2.4341
| WISTASTON HALL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.0306 | 3.346 | 3.3613 | 3.1633 | 2.975 | 2.7521 | 2.4949 | 2.2146 | 1.9257 | 1.6136 | 1.317 | 0.32218 | -1.2558 | -2.2261 | -2.5857
| WRENBURY FRITH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 0.71429 | 0.8458 | 0.82259 | 0.67155 | 0.50783 | 0.31478 | 0.1182 | -0.084117 | -0.29099 | -0.505 | -0.68518 | -1.9787 | -4.0452 | -3.862 | -3.5801
| YOCKINGS GATE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 6.5102 | 6.5284 | 6.4232 | 6.1553 | 5.8193 | 5.4516 | 5.0588 | 4.6113 | 4.1168 | 3.6085 | 3.1297 | 1.5572 | -0.36311 | -0.60454 | -0.22352
| YSBYTY GLAN CLWYD T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.602 | 3.7137 | 3.6943 | 3.4903 | 3.313 | 3.0955 | 2.8844 | 2.6829 | 2.4851 | 2.2665 | 2.0702 | 1.2459 | 0.23216 | 0.14023 | 0.31583
Grid Groups | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 33 | SWANSEA NORTH | 5.4006 | 7.5567 | 7.5977 | 2.0761 | 1.3827 | 5.8457 | -0.17464 | -4.9842 | -10.3993 | -15.4384 | -19.4703 | -33.0927 | -48.6687 | -53.0562 | -50.7883
| HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 18.2377 | 26.4048 | 25.2561 | 19.0592 | 12.2608 | 4.0107 | -4.5772 | -14.0507 | -24.9388 | -35.2163 | -43.9998 | -73.5063 | -106.5262 | -115.1024 | -110.328
| FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 33 | TRAWSFYNYDD | 5.1027 | 5.7817 | 3.9274 | 1.8296 | 9.1959 | 0.093215 | -9.0074 | -19.1087 | -30.8624 | -41.4269 | -49.9086 | -75.3059 | -101.3871 | -104.909 | -102.3826
| COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 33 | CELLARHEAD | 47.6799 | 52.9695 | 29.6183 | 14.7721 | 21.8784 | 4.074 | -6.1155 | -26.789 | -38.787 | -50.6102 | -61.6962 | -104.4975 | -162.2735 | -188.9214 | -187.7418
| GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 33 | KIRKBY | 39.9913 | 42.2717 | 42.3208 | 40.5651 | 39.0609 | 37.043 | 35.0996 | 33.2379 | 31.5476 | 29.5748 | 27.8711 | 19.4121 | 7.7441 | 1.2451 | 3.8001
| GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 33 | LISTER DRIVE | 53.4605 | 55.8876 | 55.9318 | 53.763 | 51.7775 | 49.4137 | 47.1044 | 44.468 | 42.084 | 39.306 | 36.6272 | 26.3897 | 10.3135 | 4.7011 | 5.3332
| FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 33 | KIRKBY | 7.639 | 11.0107 | 10.6505 | 34.7657 | 31.7745 | 27.056 | 20.2708 | 14.677 | 8.9321 | 3.1499 | -1.8959 | -20.8579 | -44.5202 | -55.3873 | -54.9167
| AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 33 | KIRKBY | 13.674 | 16.0398 | 16.0152 | 13.747 | 11.7879 | 9.3638 | 6.8838 | 4.3437 | 1.959 | -0.71361 | -3.179 | -13.1269 | -27.7539 | -34.0084 | -35.1953
| CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 44.2891 | 47.6743 | 47.3548 | 43.1423 | 38.8282 | 33.6166 | 28.3752 | 22.876 | 17.3523 | 11.5227 | 6.4211 | -12.6303 | -37.299 | -47.7512 | -44.3371
| LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 33 | LISTER DRIVE | 47.1083 | 52.5422 | 52.6722 | 50.6487 | 49.0855 | 45.8192 | 43.7583 | 41.8167 | 40.202 | 38.0602 | 36.2027 | 27.1385 | 13.1013 | 11.1299 | 15.5401
| BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 33 | RAINHILL | 42.7313 | 43.4336 | 43.2179 | 42.0915 | 40.9056 | 39.4022 | 37.8515 | 36.1413 | 34.3271 | 32.4338 | 30.7129 | 24.0421 | 14.7499 | 9.2196 | 8.4704
| AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 33 | KIRKBY | 24.4042 | 28.1855 | 27.2267 | 22.1829 | 16.2966 | 10.7889 | 1.3189 | -7.3591 | -16.7136 | -26.2381 | -34.5827 | -65.167 | -102.134 | -116.2988 | -114.2435
| AMLWCH GT1 / CAERGEILIOG GT1 | 33 | WYLFA | 18.4952 | 19.0035 | 17.6718 | 13.0867 | 7.8299 | 1.7679 | -4.4527 | -11.5744 | -19.5821 | -27.2462 | -33.9492 | -55.2341 | -80.9128 | -87.1865 | -85.0752
| HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | 34.3705 | 37.1874 | 36.5923 | 31.7091 | 26.9175 | 21.0845 | 15.1668 | 8.9522 | 2.4454 | -4.1643 | -9.7973 | -30.7805 | -58.7094 | -68.4221 | -67.6885
| BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 33 | RAINHILL | 22.297 | 19.944 | 13.2472 | 9.3627 | 5.6381 | 0.85694 | -3.9395 | -8.8113 | -13.5896 | -18.8386 | -23.4127 | -43.1327 | -69.1534 | -85.1437 | -80.3194
| HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 33 | BIRKENHEAD | 22.8417 | 24.825 | 23.912 | 18.9803 | 13.8199 | 7.5579 | 1.1891 | -5.6765 | -13.0786 | -20.3516 | -26.4763 | -48.0473 | -73.5447 | -83.7282 | -82.9227
| BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 33 | LEGACY | 28.3187 | 31.8011 | 30.3318 | 23.2713 | 17.2039 | 9.6642 | 2.0677 | -9.1252 | -17.1083 | -25.1738 | -32.5899 | -62.7903 | -101.9838 | -117.366 | -138.01
| CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 33 | CAPENHURST | 32.8049 | 36.704 | 35.9218 | 20.5368 | 15.2388 | 8.5324 | 1.5954 | -5.9368 | -13.934 | -21.9944 | -28.9586 | -55.2645 | -88.0972 | -103.145 | -100.4918
| DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 33 | FRODSHAM - INCE | 32.0789 | 35.6577 | 35.1625 | 32.1697 | 30.393 | 27.9344 | 25.2908 | 20.41 | 17.7898 | 15.0604 | -0.62465 | -13.2951 | -31.7772 | -41.6096 | -41.1814
| BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 33 | LISTER DRIVE | 68.4328 | 71.3976 | 71.1691 | 68.69 | 67.0841 | 65.0055 | 62.9915 | 52.823 | 50.7727 | 48.6066 | 46.0292 | 35.354 | 18.3351 | 14.9336 | 19.3305
| BANGOR GT2 / CAERNARFON GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 17.3986 | 20.1065 | 19.6347 | 15.7083 | 11.5778 | 6.7192 | 1.9485 | -3.5709 | -9.4187 | -15.3293 | -20.3667 | -38.3502 | -60.2611 | -66.0629 | -60.14
| DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 33 | CARRINGTON - FIDDLERS FERRY | 16.0845 | 19.0076 | 17.9089 | 13.0267 | 18.7441 | 14.8407 | -2.9749 | -33.6759 | -40.3608 | -47.1835 | -53.4402 | -79.1166 | -112.8329 | -129.7649 | -127.7063
| OSWESTRY GT5 / WHITCHURCH GT1 | 33 | LEGACY | 12.3187 | 14.7014 | 14.2589 | 11.1297 | 7.6906 | 3.7105 | -0.41213 | -4.9906 | -10.2964 | -15.2824 | -20.0267 | -36.2543 | -56.4805 | -61.2811 | -57.4568
| GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 33 | RAINHILL | 28.9061 | 33.0153 | 32.6289 | 28.0006 | 23.1459 | 17.0007 | 10.66 | 3.7428 | -3.4192 | -10.9504 | -17.5704 | -43.3057 | -75.4196 | -86.6294 | -84.2127
| PRENTON GRID GT1 / ROCK FERRY GT1 | 33 | BIRKENHEAD | 20.1231 | 22.5882 | 22.1066 | 21.9194 | 20.9741 | 21.6144 | 7.9302 | 3.4578 | -1.2696 | -6.1183 | -10.4085 | -26.473 | -47.3998 | -58.7475 | -55.7182
| COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 24.674 | 27.7096 | 26.7371 | 21.6208 | 16.2186 | 9.6278 | 2.6449 | -4.8152 | -13.2379 | -21.1117 | -27.5318 | -48.4215 | -73.2711 | -80.4753 | -78.2215
| BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 33 | LISTER DRIVE | 35.3334 | 41.3131 | 42.0998 | 39.4572 | 37.4286 | 34.7698 | 32.2617 | 26.2548 | 24.619 | 22.2346 | 20.0995 | 8.9157 | -7.7962 | -10.7314 | -6.6992
| ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 33 | FRODSHAM - INCE | 29.0962 | 32.9167 | 32.4263 | 28.4025 | 24.7411 | 20.4446 | 16.2961 | 7.1894 | 3.0367 | -1.2438 | -5.1808 | -20.0892 | -38.6344 | -41.5516 | -35.6425
| BOOTLE GT1 / LITHERLAND GT1A | 33 | KIRKBY | 20.6186 | 22.7682 | 22.7222 | 20.4948 | 18.6108 | 16.3421 | 14.1186 | 11.884 | 9.9458 | 7.735 | 5.6822 | -3.1738 | -15.4505 | -19.3328 | -19.0074
| BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 33 | CAPENHURST | -0.21633 | 4.0622 | 17.3877 | 12.8548 | 8.7131 | 3.5799 | -1.4841 | -12.2083 | -17.0774 | -22.252 | -26.8926 | -46.3038 | -71.7088 | -82.7703 | -80.34
| LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 33 | LEGACY | 63.2856 | 66.2077 | 64.4257 | 58.3484 | 50.4924 | 52.5813 | 41.3608 | 29.5025 | 16.1894 | 3.5254 | -7.0959 | -43.2829 | -87.1177 | -100.1422 | -97.7421
| SANKEY BRIDGES GT3 / WARRINGTON GT5 | 33 | CARRINGTON - FIDDLERS FERRY | 6.4157 | 10.058 | 10.1084 | 7.1745 | 4.3694 | 0.90953 | -2.5992 | -6.1468 | -9.5674 | -13.3854 | -16.7481 | -30.0133 | -48.3215 | -54.8195 | -52.8006
| RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 33 | RAINHILL | 25.6959 | 27.7513 | 27.6657 | 25.5419 | 23.4935 | 21.0489 | 18.6278 | 12.6594 | 10.2826 | 7.7 | 5.425 | -3.8892 | -16.7284 | -22.9904 | -21.621
| BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 18.7888 | 26.3446 | 30.8758 | 18.5747 | 17.1491 | 13.5243 | -3.5372 | -7.8349 | -12.1946 | -16.7354 | -20.6166 | -35.5362 | -54.8343 | -62.0573 | -60.5322
| BROMBOROUGH GT3 / ROCK FERRY GT2 | 33 | BIRKENHEAD | 23.5724 | 24.8835 | 24.3692 | 21.3718 | 18.5622 | 15.1354 | 11.7311 | -1.5853 | -5.128 | -8.8522 | -12.1985 | -25.4906 | -41.8506 | -48.529 | -46.3289
| WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 33 | BIRKENHEAD | 34.461 | 38.5572 | 38.8793 | 36.7408 | 34.9112 | 32.5198 | 30.0991 | 27.6054 | 25.1839 | 22.6299 | 20.6054 | 12.3558 | 1.6355 | -1.7883 | -1.7344
| ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | 27.1667 | 28.8637 | 28.2887 | 24.6784 | 20.8295 | 16.354 | 11.8852 | 5.9408 | 1.0184 | -4.0377 | -8.5785 | -25.1161 | -46.9356 | -53.7265 | -52.5877
| HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 33 | RAINHILL | 36.5594 | 36.0295 | 35.8971 | 34.5227 | 33.1724 | 31.4848 | 29.7644 | 27.9929 | 26.2386 | 24.3629 | 22.714 | 15.7439 | 6.4769 | 0.39564 | 1.8448
| DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 12.7574 | 1.7281 | 1.7375 | 0.3389 | -0.80149 | 127.8527 | 126.674 | 125.7035 | 124.9904 | 123.943 | 122.9154 | 117.573 | 109.4602 | 107.9633 | 110.2754

## High Scenario (Demand)
Demand Headroom (MW)
Return to Contents |  |  |  | High Scenario
| Group Name | Voltage (kV) | Grid / GSP Group | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050
Primary Groups | ABERDYFI T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 4.5918 | 4.6954 | 4.6604 | 4.429 | 4.1909 | 3.8879 | 3.5977 | 3.2911 | 2.9097 | 2.5766 | 2.3654 | 1.706 | 1.1557 | 0.80055 | 1.0412
| ABERGELE T1 / PENSARN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 1.8776 | 2.0791 | 1.881 | 1.1496 | 0.24473 | 0.42094 | -1.885 | -3.132 | -4.4886 | -5.8069 | -6.9631 | -10.6362 | -14.3534 | -14.3081 | -14.0635
| ABERSOCH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.1224 | 1.0824 | 0.9427 | 0.78559 | 0.10493 | -0.41302 | -0.94582 | -1.5472 | -2.282 | -2.934 | -3.5002 | -4.8613 | -6.6634 | -6.8682 | -6.5503
| ABERYSTWYTH T1 / NORTH RD T1 / PARC-Y-LLYN T1 / PARC-Y-LLYN T2 / U C WALES T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 18.5714 | 19.2506 | 19.1187 | 18.0165 | 16.8978 | 15.4907 | 14.089 | 12.5865 | 11.0434 | 9.4933 | 8.2585 | 3.3016 | -3.358 | -5.8026 | -4.5021
| ACER AVE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 0.20408 | 1.0249 | 1.0939 | 1.964 | 4.3225 | 4.186 | 0.77458 | 0.00089688 | -0.81347 | -1.6126 | -2.326 | -5.0376 | -8.4333 | -11.0376 | -10.9895
| ACORNFIELD RD T1 / DICKINSONS T1 / HAMMOND RD T1 / KODAK T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 14.9898 | 15.4094 | 15.4492 | 14.915 | 14.5562 | 14.1042 | 13.7305 | 13.4763 | 13.3658 | 13.1187 | 12.8874 | 11.1833 | 8.4324 | 7.7068 | 8.4006
| ACTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4082 | 2.6257 | 2.5972 | 2.3592 | 2.1036 | 1.7881 | 1.4702 | 1.1224 | 0.7594 | 0.37407 | 0.054845 | -1.2453 | -2.9499 | -3.9905 | -3.5746
| AIGBURTH VALE T1 / IVY AVE T1 / MATHER AVE T1 / MOSSLEY HILL T1 / WAVERTREE T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 18.1429 | 19.3926 | 19.475 | 18.7173 | 17.9867 | 17.1014 | 16.1349 | 15.1049 | 14.0723 | 12.9105 | 11.8942 | 8.1996 | 2.6869 | 0.15171 | -0.51005
| AINSDALE T1 / PINFOLD LA T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 2.6612 | 2.8948 | 2.782 | 2.2527 | 1.6736 | 0.96991 | 0.23828 | -0.57282 | -1.4763 | -2.3371 | -3.0854 | -5.5314 | -8.2806 | -8.8305 | -8.8633
| AINTREE LOCAL T1 / OLD ROAN T1 / WANGO LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 8.0918 | 8.4335 | 8.3528 | 7.5856 | 6.916 | 6.1149 | 5.327 | 4.4909 | 3.7299 | 2.9094 | 2.1557 | -0.89002 | -5.0803 | -6.8198 | -7.4131
| AIRBUS T1 / BROUGHTON RETAIL PARK T1 / MIXALLOY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 12.8469 | 13.0545 | 13.01 | 12.621 | 12.2458 | 11.7793 | 11.3156 | 10.8524 | 10.3731 | 9.8667 | 9.3957 | 7.5078 | 5.0887 | 4.4785 | 4.7372
| AIRPORT T1 / ALDERWOOD AVE (CROYDE RD) T1 / HAREFIELD RD T1 / METAL BOX (SPEKE) T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 19.5408 | 19.7952 | 19.7055 | 19.1733 | 18.6036 | 17.9723 | 17.3587 | 16.7127 | 16.0647 | 15.3686 | 14.6621 | 12.1746 | 8.3268 | 7.4808 | 7.8792
| ALBERT DOCK T1 / KINGS DOCK T1 / KINGS DOCK T2 / WAPPING T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 23.2959 | 23.5075 | 23.5176 | 23.2878 | 23.109 | 22.8869 | 22.7051 | 22.5441 | 22.4258 | 22.2571 | 22.0852 | 21.2586 | 19.8582 | 19.5727 | 19.9735
| ALLERTON T1 / ECP WEST-BANKS RD T1 / GARSTON T1 / WEAVER IND EST T1 / YEW TREE RD T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 22.9694 | 23.5261 | 23.5519 | 23.0241 | 22.5933 | 22.0679 | 21.5894 | 20.8202 | 20.216 | 19.4714 | 18.6987 | 15.8257 | 10.9892 | 9.1876 | 9.5907
| ALMATEX T1 / ST HELENS WWTW T1 / WATERY LA T2 / ex DELTA METALS T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 8.5367 | 8.9039 | 8.8829 | 8.5438 | 8.2351 | 7.8763 | 7.5301 | 7.2063 | 6.8924 | 6.5254 | 6.1547 | 4.6426 | 2.2341 | 1.6873 | 2.1747
| ALMONDS TURN T1 / ATLANTIC COMPLEX T1 / GIRO T1 / MIDLAND BANK T1 / NETHERTON T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 22.6735 | 23.0345 | 22.7325 | 21.7106 | 20.5033 | 19 | 17.4626 | 15.7357 | 13.8385 | 11.8405 | 10.0308 | 2.9076 | -6.1247 | -7.4995 | -6.1882
| ALPOCO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.2755 | 5.3357 | 5.3188 | 5.1905 | 5.0645 | 4.9209 | 4.7748 | 4.6154 | 4.4558 | 4.2964 | 4.1543 | 3.6553 | 3.0438 | 2.9314 | 2.9741
| AMLWCH T1 / AMLWCH T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 6.8469 | 6.7775 | 6.6305 | 6.1869 | 5.6721 | 5.0812 | 4.4708 | 3.7891 | 3.0036 | 2.2753 | 1.6575 | -0.18355 | -2.0992 | -2.2464 | -2.0129
| ANDERTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.6224 | 3.5918 | 3.3998 | 2.8801 | 2.5599 | 2.0285 | 0.71325 | -0.16709 | -1.1999 | -2.1772 | -3.0336 | -5.7757 | -8.9554 | -9.0157 | -8.9089
| APPLETON T1 / HORNSBRIDGE T1 / LUGSDALE T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 3.4694 | 4.1529 | 4.0447 | 3.1655 | 3.4561 | 4.7681 | -0.11072 | -1.3373 | -2.5919 | -3.9187 | -5.0753 | -9.8609 | -16.2257 | -20.5717 | -20.0883
| ARROWE PK HOSP T1 / CHAMPION PLUGS T1 / CHAMPION PLUGS T2 / WOODCHURCH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 20.5612 | 20.7962 | 20.7853 | 20.4098 | 20.1194 | 19.7834 | 19.4683 | 19.2121 | 19.0012 | 18.7141 | 18.414 | 17.0558 | 14.7852 | 14.1617 | 14.6467
| ARUNDEL T1 / GROVE PK T1 / WAVERTREE VALE T1 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 7.1735 | 7.88 | 7.9668 | 7.6922 | 7.4864 | 7.1919 | 6.8812 | 6.5796 | 6.2514 | 5.907 | 5.6764 | 4.7221 | 3.5636 | 3.5261 | 3.9698
| ASH RD T1 / KELLOGGS (WREXHAM) T1 / KELLOGGS (WREXHAM) T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.9388 | 4.3398 | 4.3154 | 3.695 | 3.1951 | 2.6184 | 2.1209 | 1.6755 | 1.3603 | 0.91978 | 0.53019 | -1.4201 | -4.4792 | -5.1749 | -4.2889
| ASSOCIATED LEAD T1 / GREAT BOUGHTON T1 / PIPERS ASH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 7.4898 | 7.9541 | 7.658 | 6.6017 | 5.3498 | 3.8327 | 2.2131 | 0.36719 | -1.6907 | -3.7052 | -5.4825 | -11.499 | -18.2388 | -18.923 | -18.6725
| ASTMOOR IND EST T1 / MACKAMAX T1 / MERSEY RD T1 / PICOW FARM RD T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 18.6939 | 19.0556 | 18.9952 | 18.5397 | 18.2772 | 17.9151 | 17.5908 | 17.3044 | 17.0782 | 16.7949 | 16.4928 | 14.8772 | 12.3143 | 11.1157 | 11.2477
| ATHOL ST T1 / CHISENHALE ST T1 / SANDHILLS LA T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 9.5531 | 9.6966 | 9.6173 | 9.2264 | 8.8141 | 8.5059 | 8.1279 | 7.7259 | 7.3091 | 6.8482 | 6.4027 | 4.8421 | 2.3214 | 1.9137 | 2.4512
| AUDLEM T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.8673 | 3.9957 | 3.9168 | 3.6792 | 3.3708 | 3.0391 | 2.6727 | 2.2535 | 1.7753 | 1.3051 | 0.89304 | -0.26262 | -1.6982 | -1.9868 | -1.6562
| BALA T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.0204 | 4.0431 | 3.9303 | 3.5216 | 3.0583 | 2.5126 | 1.9672 | 1.3516 | 0.60705 | -0.047534 | -0.55458 | -1.9184 | -3.1139 | -3.0159 | -2.6874
| BANASTRE RD T1 / DOVER RD T1 / GRANTHAM CL T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | -1.8898 | 9.5885 | 9.5467 | 8.9156 | 8.2969 | 7.5526 | 6.7673 | 5.907 | 5.0367 | 4.1419 | 3.3023 | 0.25629 | -3.9758 | -5.7786 | -6.5748
| BANGOR HOSP T1 / BANGOR UNIVERSITY T1 / EITHINOG T1 / HIRAEL T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 16.8673 | 17.3639 | 17.3192 | 16.6688 | 16.0833 | 15.3335 | 14.6123 | 13.9046 | 13.2093 | 12.491 | 11.9131 | 9.3516 | 6.2044 | 4.6725 | 5.2666
| BARBAULD ST T1 / HORROCKS LA T1 / WARRINGTON CENTRAL T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 11.1837 | 11.3211 | 11.2368 | 10.806 | 10.3896 | 9.9327 | 9.5111 | 9.0776 | 8.6428 | 8.1487 | 7.6708 | 5.9571 | 3.118 | 2.6067 | 3.32
| BARMOUTH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.0204 | 5.047 | 4.9558 | 4.6955 | 4.3767 | 4.0058 | 3.6261 | 3.1989 | 2.6815 | 2.2114 | 1.8265 | 0.70889 | -0.38203 | -0.20431 | 0.13267
| BARNSTON T1 / GAYTON T1 / IRBY T1 / THINGWALL T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 12.1531 | 12.6991 | 12.3616 | 10.7948 | 9.043 | 6.9463 | 4.7773 | 2.3773 | -0.22951 | -2.7753 | -4.9518 | -12.2405 | -20.3348 | -22.2781 | -22.4534
| BASCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.6224 | 1.8992 | 1.8829 | 1.591 | 1.2793 | 0.90385 | 0.51804 | 0.09711 | -0.32854 | -0.75657 | -1.1363 | -2.5668 | -4.5594 | -5.5751 | -5.5284
| BASS CHARRINGTON T1 / BASS CHARRINGTON T2 / CLIFTON T1 / YKK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 13.8673 | 14.4737 | 14.479 | 13.8432 | 13.2966 | 12.6009 | 11.9534 | 11.3321 | 10.819 | 10.1762 | 9.5725 | 6.7668 | 2.6101 | 0.58637 | 0.96931
| BATTERSBY LA T1 / RYLANDS ELDON ST T2 | 6 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 8.1102 | 8.1603 | 8.1369 | 8.0836 | 8.0498 | 8.0131 | 7.9577 | 7.8747 | 7.7794 | 7.69 | 7.5961 | 7.2942 | 6.8311 | 6.6536 | 6.6983
| BEAUMARIS T1 / BEAUMARIS T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.9739 | 3.9482 | 3.7985 | 3.4163 | 2.9392 | 2.4225 | 1.8958 | 1.2804 | 0.56805 | -0.10258 | -0.7073 | -2.1373 | -4.1951 | -4.4855 | -4.0127
| BEAUMONT ST T1 / DINGLE VALE T1 / LARK LA T1 / MDHB BRUNSWICK DOCK T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 8.7143 | 10.0861 | 9.7141 | 9.3779 | 9.1923 | 8.2848 | 7.9947 | 7.7645 | 7.6636 | 7.4153 | 7.2178 | 5.7191 | 3.2465 | 2.8301 | 3.8442
| BEDBURN DV T1 / BLUEBELL LA T1 / BROOKBRIDGE T1 / ECCLESTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 12.5816 | 13.3043 | 13.0715 | 11.7035 | 10.106 | 8.0886 | 5.9591 | 3.5319 | 0.88921 | -1.8114 | -4.1987 | -13.0293 | -22.6949 | -23.3244 | -22.0593
| BEECH ST T1 / LISTER DV A T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 4.5469 | 4.7749 | 4.8039 | 4.6792 | 4.5983 | 4.4827 | 4.3738 | 4.2759 | 4.2007 | 4.0996 | 4.0036 | 3.5198 | 2.8101 | 2.6312 | 2.7097
| BEMROSE T1 / CARR LA EAST T1 / LUCAS (FAZAKERLEY) T1 / NORRIS GREEN T1 / WEST DERBY T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 17.8163 | 18.7732 | 18.7428 | 17.8012 | 17.0011 | 16.0164 | 14.9827 | 13.941 | 12.9241 | 11.7905 | 10.7481 | 6.7838 | 0.76684 | -2.3425 | -3.0993
| BENTINCK ST T1 / BENTINCK ST T2 / CHESTER ST T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 10.2612 | 10.3122 | 10.1659 | 9.5654 | 8.9782 | 10.1284 | 9.5009 | 8.8322 | 8.1004 | 7.3872 | 6.723 | 4.4192 | 1.3294 | 0.77873 | 0.90657
| BERSHAM COLLIERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 1.602 | 1.6863 | 1.6786 | 1.5372 | 1.4082 | 1.2387 | 1.0621 | 0.89679 | 0.71249 | 0.53636 | 0.38436 | -0.26846 | -1.1133 | -1.5643 | -1.5506
| BERSHAM RD T1 / IND COOPE T1 / RHYD BROUGHTON LA T1 / TUTTLE ST T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 14.1939 | 14.8153 | 14.721 | 13.8895 | 13.1701 | 12.2299 | 11.3002 | 10.3665 | 9.4387 | 8.4909 | 7.7123 | 4.2765 | 0.10376 | -2.38 | -1.4292
| BETHESDA T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 3 | 3.1731 | 3.1226 | 2.8404 | 2.5297 | 2.1306 | 1.729 | 1.3042 | 0.82994 | 0.34929 | -0.031559 | -1.4381 | -3.1023 | -4.1618 | -3.7504
| BETWS-Y-COED T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.9694 | 3.8968 | 3.7365 | 3.2353 | 2.6691 | 2.0132 | 1.3796 | 0.65201 | -0.21886 | -0.98833 | -1.6047 | -3.1464 | -4.7857 | -4.8651 | -4.5861
| BEWSEY T1 / OWEN ST T1 / RODNEY ST T1 / RYLANDS ELDON ST T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 13.8061 | 14.3234 | 14.2777 | 13.5333 | 12.8486 | 12.0455 | 11.2768 | 10.5074 | 9.7709 | 8.9646 | 8.2248 | 5.282 | 0.93179 | -0.22194 | 0.17834
| BIBBYS T1 / INLAND REVENUE OFFICES T1 / REGENT RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 5.6224 | 6.1282 | 6.1519 | 8.1595 | 7.7649 | 7.3738 | 6.9657 | 5.6876 | 5.3745 | 4.988 | 4.6524 | 3.0399 | 0.92388 | 0.48121 | 0.5735
| BICC HUYTON QUARRY T1 / TARBOCK T1 / WHISTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 11.7143 | 11.8798 | 11.7103 | 11.0796 | 10.3303 | 9.4286 | 8.5113 | 7.4742 | 6.3749 | 5.2241 | 4.1635 | 0.12208 | -4.8624 | -5.2381 | -4.7833
| BICC WREXHAM T1 / MARCHWIEL T1 / WIE CENTRAL T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 6.898 | 7.2789 | 7.3074 | 6.8654 | 6.5842 | 6.2315 | 5.9471 | 5.7621 | 5.7099 | 5.5378 | 5.3558 | 4.0186 | 1.7885 | 1.2641 | -22.9798
| BIRKENHEAD CENTRAL T1 / SINGLETON AVE T1 / TRANMERE T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 9.5673 | 9.7948 | 9.7368 | 9.3454 | 8.8776 | 8.4985 | 8.1263 | 7.5841 | 7.0502 | 6.4791 | 5.8851 | 3.6811 | 0.57209 | -0.26798 | -0.1315
| ex BIXTETH ST T1 / LITTLEWOODS T1 / PALL MALL T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 3.8633 | 3.9715 | 3.9258 | 3.7187 | 3.4693 | 3.2141 | 2.9552 | 2.6844 | 2.4034 | 2.0812 | 1.7607 | 0.70724 | -1.0602 | -1.3276 | -0.87567
| BLACON T1 / COCOA BARRY T1 / CRANE BANK T1 / KNUTSFORD WAY T1 / TOWER WHARF T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 16.2245 | 17.0705 | 16.993 | 16.0245 | 15.091 | 13.8883 | 12.7012 | 11.4745 | 10.3116 | 9.0481 | 7.9512 | 2.9866 | -3.492 | -7.5034 | -6.3265
| BLAENAU FFESTINIOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.6939 | 1.7945 | 1.7716 | 1.6491 | 1.5194 | 1.3468 | 1.1739 | 0.98944 | 0.78203 | 0.57317 | 0.40677 | -0.26892 | -0.9166 | -1.2601 | -0.92045
| BLUNDELL ST T1 / ROPEWALKS T1 / ST JAMES T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 9.0198 | 9.4276 | 9.4701 | 9.2325 | 9.0902 | 8.8885 | 8.723 | 8.6236 | 8.6088 | 8.5213 | 8.4313 | 7.6166 | 6.2072 | 5.8705 | 6.3598
| BLUNDELLSANDS (NORTH) T1 / BLUNDELLSANDS (SOUTH) T1 / CROSBY T1 / KERSHAW AVE T1 / WATERLOO T2 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 15.9898 | 16.8645 | 16.5027 | 14.999 | 13.1904 | 10.958 | 8.5995 | 5.9389 | 3.007 | 0.0033533 | -2.6363 | -12.1456 | -23.1013 | -24.9578 | -23.5844
| BODFARI PRODUCERS T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.6122 | 4.7189 | 4.7298 | 4.6451 | 4.5911 | 4.5137 | 4.4598 | 4.4059 | 4.3906 | 4.35 | 4.3031 | 3.9994 | 3.4633 | 3.2851 | 3.4067
| BOLTON ST T1 / GREEK ST T1 / HPO COPPERAS HILL T1 / OLDHAM PLACE T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.8061 | 5.322 | 5.3686 | 4.8722 | 4.5729 | 4.1868 | 3.8984 | 3.6806 | 3.5769 | 3.3783 | 3.1691 | 1.7763 | -0.50424 | -1.0937 | -0.4975
| BOOTLE GRID T1 / KELLOGGS T1 / PACIFIC RD T1 / WASHINGTON ST T1 / WATERLOO T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | 18.4388 | 19.0863 | 19.0625 | 18.1407 | 17.3505 | 16.3744 | 15.4431 | 14.4966 | 13.6885 | 12.7763 | 11.9545 | 8.1682 | 3.2825 | 1.9062 | 1.7232
| BOOTLE GRID T2 / ORRELL MOUNT T1 / SCARISBRICK AVE T1 / TATTON RD T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | 14.4082 | 15.1102 | 15.0068 | 14.1783 | 13.4239 | 12.5305 | 11.5774 | 10.5425 | 9.5051 | 8.3922 | 7.3383 | 3.4999 | -2.0912 | -4.3621 | -4.7933
| BOTWNNOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.2041 | 5.2757 | 5.2386 | 5.0684 | 4.8752 | 4.6561 | 4.4271 | 4.18 | 3.888 | 3.6321 | 3.4388 | 2.8715 | 2.1685 | 1.8551 | 1.9124
| BOULEVARD T1 / CHAPELFORD T1 / HAWLEYS LA T1 / WESTBROOK T1 / WINWICK QUAY T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 16.2857 | 17.0362 | 16.9741 | 15.9736 | 15.0498 | 13.908 | 12.8038 | 11.7103 | 10.7267 | 9.6012 | 8.5817 | 4.1822 | -2.1246 | -5.6333 | -5.2446
| BOW ST T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.6735 | 2.8102 | 2.7048 | 2.3107 | 1.8162 | 1.6302 | 0.6699 | -0.014426 | -0.75819 | -1.4864 | -2.1373 | -4.213 | -6.5414 | -6.9139 | -6.7467
| BOWATER CONTAINERS T1 / ELLESMERE PORT LOCAL T1 / HH ROBERTSONS T1 / MOBIL OIL (E PORT) T1 / WHITBY T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 6.9082 | 7.5628 | 7.491 | 6.5913 | 5.9128 | 5.032 | 4.2098 | 3.4165 | 2.6681 | 1.8516 | 1.0952 | -2.2152 | -7.1578 | -9.4975 | -9.9555
| BR STATION T1 / DUCHY RD T1 / ELECTRA WAY T1 / MIDLAND ROLLMAKERS T1A / NORTH WESTERN MILLS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 12.7347 | 13.4245 | 8.3114 | 7.1533 | 6.2604 | 1.02 | -0.045426 | -1.0696 | -1.9647 | -2.9807 | -3.9671 | -8.7727 | -15.3189 | -18.3967 | -17.4973
| BRD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.1327 | 2.2712 | 2.2152 | 1.8347 | 1.4547 | 0.99691 | 0.54103 | 0.053123 | -0.45382 | -0.9498 | -1.358 | -3.2613 | -6.3264 | -6.4303 | -6.3014
| BRITISH ALUMINIUM LATCHFORD T1 / GREENHALL WHITLEY T1 / LATCHFORD T1 / LATCHFORD T2 / THAMES BOARD MILL T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 11.8367 | 12.7118 | 12.7782 | 12.1513 | 11.655 | 11.0288 | 10.4127 | 9.8525 | 9.3878 | 8.7955 | 8.272 | 5.7763 | 1.9924 | 0.6271 | 0.80638
| BRITISH OXYGEN T1 / WINDLEHURST T1 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 2.8041 | 3.1316 | 3.4826 | 3.5885 | 2.6338 | 2.3589 | 2.0608 | 0.20406 | -0.14612 | -0.53873 | -0.90969 | -2.1509 | -4.1886 | -4.8133 | -4.5912
| BRITISH PIPE ASSOCIATION T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 3.9388 | 4.0355 | 4.0263 | 3.8903 | 3.7725 | 3.617 | 3.4949 | 3.3954 | 3.3077 | 3.1829 | 3.0672 | 2.5425 | 1.659 | 1.4776 | 1.6927
| BRITISH SIDAC T1 / SHERDLEY RD T1 / ST HELENS LINKWAY T1 / WATERY LA T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 9.6592 | 9.8972 | 9.7723 | 21.0479 | 20.4633 | 19.728 | 19.0107 | 18.2448 | 17.4579 | 16.6504 | 15.9481 | 12.9201 | 9.2033 | 6.2731 | 7.238
| BROADGREEN T1 / CROXTETH T1 / EAST PRESCOT RD (FINCH LA) T1 / KNOTTY ASH T1 / LEYFIELD RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 12.102 | 13.6078 | 13.7149 | 12.77 | 11.948 | 10.9008 | 9.8035 | 8.6716 | 7.6212 | 6.4025 | 5.3115 | 0.95002 | -5.5501 | -8.5093 | -9.1356
| BROMFIELD T1 / BROMFIELD T2 / PONTERWYL T1 / RHYD-Y-GOLEU T1 / SYNTHITE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 22.1224 | 22.7348 | 22.6305 | 21.6112 | 20.6114 | 19.3745 | 18.1337 | 16.8104 | 15.4724 | 14.1119 | 12.9619 | 8.6147 | 3.2234 | 0.35243 | 0.0086098
| BROOK LA T1 / MANNINGS LA T1 / NEWTOWN CHESTER T1 / UPTON HEATH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 12.1327 | 13.0414 | 12.8734 | 11.9121 | 10.9252 | 9.6426 | 8.2538 | 6.7316 | 5.1102 | 3.4748 | 2.0342 | -3.519 | -9.8452 | -13.7626 | -13.01
| BROOK ST T1 / KINGSWAY TUNNEL T1 / NWWA SANDON DOCK T1 / NWWA SANDON DOCK T2 | 11 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 17.1224 | 17.4849 | 17.49 | 17.0292 | 16.68 | 16.3639 | 16.0629 | 15.8198 | 15.675 | 15.4432 | 15.1886 | 13.7507 | 11.4267 | 10.8917 | 11.3679
| BRYN STANLEY T1 / DENBIGH T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.2857 | 4.4472 | 4.3772 | 3.9621 | 3.5486 | 3.0393 | 2.5104 | 1.9663 | 1.3823 | 0.79187 | 0.2849 | -1.6311 | -4.0332 | -4.9788 | -4.8435
| BUCKINGHAM ST T1 / EVERTON RD T1 / SUBURBAN RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 8.6633 | 9.221 | 9.3161 | 9.1642 | 9.0786 | 8.9061 | 8.7862 | 8.6882 | 8.6608 | 8.5755 | 8.4978 | 7.9059 | 7.0419 | 6.9425 | 7.2747
| BUCKLEY T1 / BUCKLEY T2 / BUCKLEY CROSS T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 8.4694 | 8.9653 | 8.8543 | 8.0374 | 7.1774 | 6.126 | 5.0481 | 3.8529 | 2.6637 | 1.4437 | 0.38679 | -3.5705 | -8.514 | -11.3803 | -11.7923
| BUILDWAS RD T1 / MORGAN REFRACTORIES T1 / NESTON MAIN T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 11.1735 | 11.2759 | 11.0434 | 10.1695 | 9.1646 | 7.9928 | 6.7974 | 5.4503 | 3.9899 | 2.5526 | 1.312 | -2.7953 | -7.3816 | -7.5949 | -7.4217
| BURLINGTON AVE T1 / FRESHFIELD T1 / MARSH BROWS T1 / SOUTHPORT RD T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 13 | 13.5936 | 13.4215 | 12.3469 | 11.2102 | 9.8356 | 8.3983 | 6.831 | 5.25 | 3.6168 | 2.1806 | -3.022 | -9.4521 | -13.2276 | -13.6262
| BURMAH OIL T1 / CABOT CARBON T1 / VAN LEER NO 1 T1 | 7 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 1.7673 | 1.9047 | 1.9159 | 1.776 | 1.6727 | 1.5452 | 1.455 | 1.3824 | 1.3641 | 1.3018 | 1.2415 | 0.75809 | -0.076011 | -0.33285 | -0.11709
| BUTLINS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.5306 | 4.661 | 4.6772 | 4.5891 | 4.5323 | 4.448 | 4.3715 | 4.3142 | 4.2699 | 4.1956 | 4.137 | 3.8159 | 3.3189 | 3.1286 | 3.289
| BUTTINGTON CROSS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.398 | 3.5391 | 3.5269 | 3.3546 | 3.2344 | 3.0666 | 2.9166 | 2.785 | 2.6674 | 2.5338 | 2.4038 | 1.7397 | 0.80071 | 0.48639 | 0.53043
| BXL BROMBOROUGH T1 / TULIP T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 3.2551 | 3.4041 | 3.3961 | 3.0591 | 2.8179 | 2.5143 | 2.2508 | 2.0213 | 1.8407 | 1.6244 | 1.4127 | 0.31911 | -1.1869 | -1.4749 | -1.2715
| CABLE ST T1 / GRADWELL ST T2 / OLDHAM PLACE T2 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 5.6837 | 6.222 | 6.2889 | 5.8874 | 5.6385 | 5.3409 | 5.1166 | 4.9535 | 4.6926 | 4.5218 | 4.0954 | 2.1059 | -1.1539 | -1.0965 | -0.14953
| CABLE ST T2 / CROWN COURTS T1 / GRADWELL ST T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 10.2653 | 10.3968 | 10.2803 | 9.6591 | 9.291 | 8.7991 | 8.3172 | 7.8636 | 7.4142 | 6.9191 | 6.4339 | 4.7639 | 2.2138 | 2.2456 | 3.1954
| CADBURYS KRONOSPAN T1 / CADBURYS KRONOSPAN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.6531 | 3.8505 | 3.7881 | 3.4444 | 3.095 | 2.663 | 2.2333 | 1.7911 | 1.3332 | 0.84719 | 0.42227 | -1.203 | -3.3469 | -3.504 | -3.1481
| CADBURYS T1 / CADBURYS T2 / HOPFIELD RD T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 8.7551 | 9.2658 | 9.2688 | 8.8454 | 8.5448 | 8.1483 | 7.7617 | 7.3832 | 7.0493 | 6.6594 | 6.3169 | 4.7114 | 2.4001 | 1.6496 | 1.8762
| CAERGEILIOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5 | 3.5319 | 3.4243 | 3.0548 | 2.5253 | 2.0444 | 1.5445 | 0.81672 | -0.012176 | -0.81873 | -1.57 | -3.9002 | -6.6807 | -7.2958 | -7.0639
| CAERGWRLE T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 1.5816 | 1.7758 | 1.6795 | 1.3363 | 2.3113 | 2.4185 | -1.0555 | -2.0191 | -3.0852 | -4.165 | -5.1352 | -8.2258 | -11.8443 | -12.4591 | -12.1503
| CAERNARFON T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 1.9592 | 2.1204 | 2.0757 | 1.7836 | 1.464 | 1.0958 | 0.7367 | -0.073456 | -0.806 | -1.5832 | -2.3443 | -4.9936 | -8.2418 | -8.6225 | -8.2849
| CAERSWS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 4.3469 | 4.4511 | 4.407 | 4.1632 | 3.8868 | 3.5647 | 3.2218 | 2.8621 | 2.4391 | 2.0589 | 1.7439 | 0.72959 | -0.51855 | -0.79815 | -0.74157
| CALDY T1 / HOYLAKE T1 / MEOLS T1 / WEST KIRBY SOUTH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 14.6531 | 15.1977 | 15.0053 | 13.6966 | 12.4428 | 10.8441 | 9.2719 | 7.6215 | 5.7556 | 4.0259 | 2.7122 | -1.7953 | -6.9589 | -10.5381 | -10.5301
| CARBORUNDUM T1 / HOUGHTONS LA T1 / RAINFORD T1 / WINDLEHURST T2 | 11 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 12.8469 | 13.5638 | 13.4242 | 12.3248 | 11.1613 | 9.7506 | 8.3074 | 6.7511 | 5.1892 | 3.5582 | 2.1271 | -3.4933 | -10.8454 | -15.5879 | -15.5776
| CARLTON ST T1 / CARLTON ST T2 / CHALON WAY T2 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 8.2 | 8.5116 | 8.4886 | 8.0253 | 7.6581 | 7.1978 | 6.7814 | 6.3967 | 6.0332 | 5.6456 | 5.3146 | 3.7503 | 1.5271 | 0.70349 | 0.78405
| CARMEL T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.051 | 1.1827 | 1.1194 | 0.95707 | 0.70611 | 0.42435 | 0.11298 | -0.26258 | -0.69507 | -1.1308 | -1.5322 | -2.7486 | -4.2254 | -4.2818 | -3.9053
| CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 11 | CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 16.9592 | 17.9007 | 17.9095 | 16.8407 | 15.9052 | 14.732 | 13.5755 | 12.4004 | 11.2208 | 10.0009 | 9.0038 | 5.2538 | 0.10686 | -2.1492 | -2.7243
| CEFN MAWR T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.9388 | 3.9891 | 3.8488 | 3.417 | 2.8902 | 2.2989 | 1.6878 | 1.0013 | 0.17125 | -0.59584 | -1.2501 | -3.0402 | -5.1414 | -5.7333 | -5.9245
| CEMAES BAY T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 2.2959 | 2.2827 | 2.1963 | 1.9761 | 1.7134 | 1.4238 | 1.112 | 0.76263 | 0.35786 | -0.012856 | -0.34525 | -1.276 | -2.3409 | -2.4953 | -2.35
| CEMMAES RD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.4898 | 1.5321 | 1.4572 | 1.0755 | 0.70339 | 0.3514 | -0.18676 | -0.67694 | -1.2645 | -1.7703 | -2.1646 | -3.4482 | -4.6355 | -4.9647 | -5.4786
| CEREAL PARTNERS T1 / LEVER GEORGIA AVE T1 / POOL LA T1 / UML LEVER BROMBOROUGH T2 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 20.6224 | 20.893 | 20.9103 | 20.5851 | 20.3486 | 20.0506 | 19.8168 | 19.6439 | 19.5521 | 19.3669 | 19.1866 | 18.0791 | 16.1788 | 15.5264 | 15.8643
| CHALON WAY T1 / TECHNOLOGY CAMPUS T1 / WOODVILLE ST T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 1.5898 | 2.7356 | 2.7027 | 2.2857 | 1.9021 | 1.4502 | 1.0121 | 0.56577 | 0.14548 | -0.3161 | -0.75657 | -2.5703 | -5.0929 | -6.1193 | -6.5416
| CHESHIRE GREEN T1 / NWF T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 4.3265 | 4.4409 | 4.3817 | 4.0581 | 3.8147 | 3.511 | 3.2209 | 2.9663 | 2.7254 | 2.4645 | 2.2141 | 1.05 | -0.58533 | -1.2413 | -1.082
| CHESTER GATES T1 / UNILEVER DUNKIRK T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 4.2245 | 17.8703 | 17.8689 | 17.6194 | 17.4238 | 17.1701 | 16.9711 | 16.567 | 16.4094 | 16.2273 | 16.0646 | 15.2792 | 14.1221 | 13.735 | 13.9133
| CHESTER ST (WREXHAM) T1 / EAGLES MEADOW T1 / RHOSNESNI T1 / WHITEGATE T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 16.2143 | 16.8242 | 16.7066 | 15.9161 | 15.1064 | 14.0619 | 12.9884 | 11.852 | 10.6722 | 9.4928 | 8.5148 | 4.4671 | -0.29409 | -3.4826 | -2.7749
| CHILDWALL T1 / CHILDWALL FIVEWAYS T1 / LYNDENE RD T1 / MIDDLEMASS HEY T1 / NAYLORS RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 13.4898 | 14.7165 | 14.6661 | 13.601 | 12.5226 | 11.1113 | 9.6997 | 8.2089 | 6.6902 | 5.0882 | 3.7545 | -1.8388 | -9.1069 | -14.29 | -12.8237
| CHOWLEY T1 / CHOWLEY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.2143 | 3.4807 | 3.4253 | 2.9986 | 2.5419 | 1.9955 | 1.4263 | 0.80565 | 0.17708 | -0.45869 | -0.99305 | -3.0205 | -5.6266 | -6.9709 | -6.9501
| CHURCH LA T1 / NANT HALL T1 / PRESTATYN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 10.5102 | 10.8644 | 10.7118 | 9.9573 | 9.1051 | 8.0654 | 6.998 | 5.7923 | 4.4702 | 3.2201 | 2.1698 | -1.2073 | -4.6258 | -5.0413 | -4.8896
| CHURCH LAWTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.7347 | 3.8988 | 3.806 | 3.4847 | 3.177 | 2.7721 | 2.3453 | 1.8622 | 1.328 | 0.81876 | 0.35234 | -1.2987 | -3.1352 | -4.3149 | -4.4513
| CHURCH ST WINSFORD T1 / OVER T1 / WHARTON PK T1 / WOODFORD PK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 11.8061 | 12.5961 | 12.495 | 11.4093 | 10.2878 | 8.8851 | 7.4608 | 5.9591 | 4.4012 | 2.8504 | 1.572 | -3.4114 | -9.5037 | -13.3953 | -13.0161
| CIVIC CENTRE T1 / CLAUGHTON AVE T1 / ELECTRICITY ST T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.4147 | 12.4111 | 12.0839 | 11.0935 | 10.5274 | 9.7646 | 8.9589 | 8.087 | 7.1683 | 6.3863 | 5.542 | 1.9874 | -2.772 | -5.3134 | -5.8318
| CLEDFORD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.4184 | 1.8284 | 1.8503 | 1.6106 | 1.3907 | 1.1129 | 0.79721 | 0.47175 | 0.13383 | -0.2291 | -0.54543 | -1.7467 | -3.4376 | -4.6528 | -4.6346
| CLOCKFACE T1 / GEC ST HELENS T1 / HILLS MOSS T1 / NCB SUTTON MANOR T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 16.898 | 17.2855 | 17.1829 | 16.4675 | 15.7609 | 14.8824 | 14.0309 | 13.175 | 12.3391 | 11.4213 | 10.6241 | 7.1223 | 2.3572 | -0.85219 | -0.10779
| CLUBMOOR T1 / DUNLOPS WALTON T1 / WALTON T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 10.1531 | 10.3547 | 10.3656 | 10.1032 | 9.9348 | 9.7701 | 9.6234 | 9.5158 | 9.4743 | 9.3682 | 9.2633 | 8.5542 | 7.3616 | 7.0595 | 7.3839
| CLUBMOOR T2 / LISTER DV A T1 / SUBURBAN RD T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 6.5202 | 7.0173 | 7.0739 | 6.8211 | 6.6172 | 6.352 | 6.0955 | 5.6041 | 5.4039 | 5.141 | 4.9043 | 3.7626 | 2.0907 | 1.7519 | 2.0089
| COEDPOETH T1 / COEDPOETH T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.4592 | 4.6088 | 4.4819 | 4.0561 | 3.528 | 3.9215 | 2.2338 | 1.4813 | 0.64659 | -0.15698 | -0.84801 | -3.2986 | -5.4569 | -4.5284 | -3.6191
| COLWYN BAY T1 / COLWYN BAY T2 / RHOS-ON-SEA T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 11.2041 | 11.5086 | 11.5046 | 11.1959 | 10.9368 | 10.6134 | 10.2797 | 9.961 | 9.6426 | 9.2848 | 8.9622 | 7.3723 | 4.0045 | 3.2844 | 3.29
| CONEY GREEN T1 / OSWESTRY T2 / OSWESTRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 8.3571 | 9.3321 | 9.3444 | 9.0119 | 8.6467 | 8.1445 | 7.5777 | 6.9525 | 6.2326 | 5.5086 | 4.9491 | 2.7799 | 0.10001 | -2.1122 | -1.5163
| CONIX T1 / CONIX T2 / MEDEVA T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 12.6939 | 12.9104 | 12.9215 | 12.6892 | 12.5294 | 12.3374 | 12.181 | 12.0845 | 12.0497 | 11.959 | 11.8571 | 11.0897 | 9.7776 | 9.4076 | 9.7579
| CONNAHS QUAY LOCAL T1 / CONNAHS QUAY LOCAL T2 / HAWARDEN T1 / KING GEORGE ST T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 12.9898 | 13.8699 | 13.7527 | 12.7421 | 11.6636 | 10.294 | 8.8854 | 7.37 | 5.762 | 4.1306 | 2.7654 | -2.2505 | -8.7328 | -13.4581 | -13.3348
| CONWY T1 / DEGANWY T1 / LLANDUDNO JUNCTION T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 14.9731 | 15.528 | 15.3246 | 14.3108 | 13.1329 | 11.6911 | 10.2072 | 8.5389 | 6.6027 | 4.7716 | 3.2425 | -1.7491 | -6.8192 | -6.9664 | -7.0036
| CORWEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.551 | 3.6323 | 3.5591 | 3.202 | 2.8386 | 2.3986 | 1.9712 | 1.5064 | 1.005 | 0.53395 | 0.13881 | -1.2695 | -2.8266 | -3.4787 | -3.6453
| CREWE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.3469 | 2.9122 | -3.1059 | -3.0957 | -3.0957 | -3.1389 | -3.2083 | -3.3043 | -3.4112 | -3.5374 | -3.6283 | -4.6981 | -6.218 | -5.8454 | -5.4707
| CRIGGION RADIO STATION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.1939 | 2.2246 | 2.1976 | 2.098 | 1.9913 | 1.8713 | 1.7592 | 1.6353 | 1.5202 | 1.3876 | 1.2657 | 0.82129 | 0.19327 | 0.033975 | 0.1401
| CROSSFIELDS T1 / CROSSFIELDS T2 / LEVERS CROSSFIELDS T3 / GATEWARTH SEWAGE T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 21.6122 | 22.0566 | 22.1159 | 21.9093 | 21.7566 | 21.5468 | 21.3542 | 21.1777 | 21.0619 | 20.871 | 20.6993 | 19.7916 | 18.3602 | 17.9925 | 18.2953
| CROWTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 3.6531 | 3.8364 | 3.8207 | 3.5988 | 3.355 | 3.0739 | 2.7704 | 2.4423 | 2.1134 | 1.7681 | 1.4629 | 0.38491 | -1.0703 | -1.7857 | -1.875
| CWM DYLI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.6633 | 2.6703 | 2.6453 | 2.5134 | 2.3987 | 2.2449 | 2.1072 | 1.9749 | 1.8038 | 1.6697 | 1.5975 | 1.3959 | 1.2743 | 1.2093 | 1.2675
| DAILY POST & ECHO T1 / DAILY POST & ECHO T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.6286 | 5.1162 | 5.2317 | 5.2386 | 5.2694 | 5.3318 | 5.3516 | 5.3684 | 5.3858 | 5.4066 | 5.4033 | 5.4072 | 5.3329 | 5.3256 | 5.4242
| DARESBURY NPL T1 / DARESBURY NPL T2 / DARESBURY PK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 4.7143 | 4.8218 | 4.7602 | 4.4614 | 4.1498 | 3.7912 | 3.4426 | 3.0812 | 2.7166 | 2.3343 | 1.975 | 0.63459 | -1.2068 | -1.7987 | -1.672
| DAVY WAY T1 / LLAY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.0102 | 2.2653 | 2.2582 | 1.9316 | 1.6549 | 1.3119 | 0.98538 | 0.68485 | 0.41728 | 0.10346 | -0.16629 | -1.4535 | -3.3669 | -4.3688 | -4.0888
| DEESIDE ALUMINIUM T1 / DUNLOP PLASTICS T1 / FIRESTONE T1 / TETRAPAK T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.898 | 3.7382 | 3.8036 | 2.9451 | 2.3594 | 1.6241 | 1.0406 | 0.62513 | 0.48243 | 0.080047 | -0.3278 | -3.1949 | -8.044 | -9.3404 | -8.0072
| DEESIDE IND PK T1 / DEESIDE IND PK 6TH AVE T1 / RAF SEALAND T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 7.2041 | 7.5403 | 7.4749 | 6.9303 | 6.391 | 5.7695 | 5.1878 | 4.6143 | 4.0809 | 3.4577 | 2.8504 | 0.29084 | -3.197 | -3.6487 | -2.8694
| DELAMORE ST T1 / KIRKDALE T1 / WALTON T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 4.6755 | 5.7061 | 5.8519 | 5.5242 | 7.8153 | 7.3915 | 6.9747 | 5.7141 | 5.2832 | 4.7939 | 4.3847 | 2.6659 | 0.48594 | -0.11109 | -0.3606
| DESOTO RD T1 / MERSEY BRIDGE T1 / PITT ST T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 14.4898 | 14.7189 | 14.744 | 14.5801 | 14.4694 | 14.3333 | 14.2203 | 14.1338 | 14.0905 | 14.0154 | 13.9319 | 13.394 | 12.4879 | 12.296 | 12.575
| DIBBINSDALE T1 / PLYMYARD T1 / WIBP HARDKNOTT RD T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 8.7857 | 9.0117 | 8.8507 | 8.1009 | 7.341 | 6.4366 | 5.5116 | 4.5382 | 3.5251 | 2.4596 | 1.4885 | -2.1297 | -6.6262 | -7.5773 | -7.0505
| DINGLE T1 / GRANBY T1 / ST JAMES T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 11.9898 | 12.3045 | 12.3458 | 12.1924 | 12.0808 | 11.9369 | 11.7929 | 11.6729 | 11.5732 | 11.446 | 11.3455 | 10.7911 | 9.9765 | 9.7736 | 9.9146
| DITTON T1 / GAVIN RD T1 / HOUGH GREEN T1 / RTZ T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 12.5204 | 13.1537 | 13.028 | 12.0776 | 11.1167 | 9.9145 | 8.7093 | 7.4896 | 6.2733 | 4.967 | 3.8132 | -1.0114 | -7.5239 | -12.0445 | -11.0446
| DODDS LA T1 / HOLBORN HILL T1 / MAGHULL T1 / MAGHULL T2 / ROBBINS BRIDGE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 13.4898 | 15.3436 | 15.2416 | 13.9456 | 12.3753 | 10.409 | 8.2418 | 5.7508 | 3.0624 | 0.40973 | -1.8284 | -9.7985 | -19.4565 | -26.5301 | -26.751
| DOLGARROG T1 / DOLGARROG T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.051 | 3.0807 | 2.982 | 2.6114 | 2.1929 | 1.725 | 1.2597 | 0.74542 | 0.16323 | -0.37773 | -0.84332 | -2.1868 | -3.8622 | -4.2201 | -3.8779
| DOLGELLAU T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.4082 | 3.4772 | 3.3554 | 2.8779 | 2.3746 | 1.7561 | 1.1467 | 0.47306 | -0.3623 | -1.0775 | -1.6002 | -3.0215 | -4.1815 | -4.0398 | -3.8232
| DUCKINGTON T1 / DUCKINGTON T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.8418 | 4.952 | 4.8483 | 4.4413 | 3.9778 | 3.4635 | 2.8974 | 2.2819 | 1.5886 | 0.92323 | 0.33302 | -1.6283 | -3.82 | -4.0579 | -3.8491
| DUDDON T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 5.3061 | 5.3735 | 5.3594 | 5.2088 | 5.068 | 4.9042 | 4.7344 | 4.5622 | 4.3851 | 4.2065 | 4.05 | 3.4213 | 2.5779 | 2.1828 | 2.161
| DYFFRYN ARDUDWY T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.3265 | 5.2745 | 5.1965 | 4.8487 | 4.4944 | 4.0786 | 3.6762 | 3.2334 | 2.733 | 2.2989 | 1.9801 | 1.0547 | 0.22861 | 0.15203 | 0.035185
| DYSERTH RD T1 / FFORDD LAS T1 / FFORDD LAS T2 / WESTBOURNE AVE T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 10.9082 | 12.5812 | 12.6986 | 12.0571 | 11.3236 | 10.2659 | 9.1458 | 7.8682 | 6.4145 | 5.0733 | 4.1328 | 0.7596 | -2.6039 | -5.4359 | -4.7665
| EDEN VALE T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.0306 | 3.2421 | 3.23 | 3.0151 | 2.7766 | 2.4948 | 2.2023 | 1.8844 | 1.5581 | 1.2257 | 0.92714 | -0.44297 | -3.0702 | -3.3611 | -3.165
| EDERN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 0.84694 | 0.75327 | 1.0497 | 0.43759 | 0.17428 | 0.13091 | -1.7596 | -2.5031 | -3.3965 | -4.181 | -4.8194 | -6.5336 | -8.2308 | -8.4144 | -8.1652
| EDGE HILL T1 / LIVERPOOL UNIVERSITY T1 / LIVERPOOL UNIVERSITY T2 / LIVERPOOL UNIVERSITY T3 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 13.6837 | 14.2017 | 14.1812 | 13.5916 | 13.057 | 12.4274 | 11.8652 | 11.3255 | 10.8621 | 10.2702 | 9.6629 | 7.1854 | 3.0655 | 2.2965 | 3.3049
| EDGE LA (TAPLEY PLACE) T1 / LISTER DV B T3 / MILL LA (WAVERTREE) T1 / PLESSEY (EDGE LA) T1 / STONEYCROFT T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 16.449 | 18.3813 | 18.7143 | 18.5803 | 18.4242 | 18.204 | 17.8619 | 17.4411 | 17.0204 | 16.5144 | 16.1213 | 14.4399 | 12.1058 | 12.3353 | 13.4101
| EGA ELECTRIC T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4 | 4.0578 | 3.9923 | 3.722 | 3.4373 | 3.1141 | 2.7749 | 2.4168 | 2.018 | 1.6187 | 1.2799 | 0.12342 | -1.1933 | -1.3504 | -1.1902
| EGERTON T1 / ROCK FERRY T1 / SHELL TRANMERE T1 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | 5.602 | 6.0732 | 5.9931 | 5.3662 | 4.8955 | 4.3428 | 3.7967 | 3.2565 | 2.7127 | 2.105 | 1.5384 | -0.66294 | -3.999 | -5.0031 | -4.7463
| EGREMONT T1 / LISCARD T1 / POULTON T1 / STONE MANGANESE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 13.2857 | 14.2545 | 14.3957 | 14.0137 | 13.7337 | 13.341 | 12.9742 | 12.6708 | 12.4358 | 12.0998 | 11.824 | 10.2681 | 7.7905 | 7.0748 | 7.643
| ELLESMERE T1 / MMB ELLESMERE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.5918 | 1.7834 | 1.6984 | 1.223 | 0.743 | 0.15436 | -0.42438 | -1.0304 | -1.6758 | -2.3091 | -2.8387 | -4.8782 | -7.519 | -8.9989 | -8.6856
| ELTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 4.7755 | 4.7155 | 4.5795 | 4.2486 | 3.8707 | 3.4397 | 3.0018 | 2.4931 | 1.9453 | 1.4145 | 0.8919 | -0.83748 | -2.8228 | -3.0755 | -2.9849
| ENGINEER PK T1 / PILKINGTONS QUEENSFERRY T1 / QUEENSFERRY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 5.6429 | 6.0843 | 6.0762 | 5.4774 | 5.0121 | 4.4228 | 3.8859 | 3.4149 | 3.0307 | 2.5468 | 2.1173 | -0.079858 | -3.356 | -4.7748 | -4.1201
| ESTUARY COMMERCE PK T1 / LEEWARD DR T1 / LEEWARD DR T2 / SPEKE HALL RD T1 / SPEKE SKY PK T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 21.1633 | 21.4255 | 21.437 | 21.1321 | 20.9118 | 20.6299 | 20.4123 | 20.2454 | 20.1557 | 20.0031 | 19.843 | 18.7959 | 17.1308 | 16.7077 | 17.0675
| EVERTON BROW T1 / GARDNERS ROW T1 / SHEIL PK T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 6.5408 | 7.7118 | 7.9633 | 8.0274 | 8.1152 | 7.9385 | 7.9134 | 7.8631 | 7.8366 | 7.7559 | 7.7264 | 7.3651 | 6.8591 | 6.8712 | 7.1573
| EXPRESS FOODS T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 5.9898 | 6.0376 | 6.0214 | 5.9444 | 5.867 | 5.7795 | 5.6832 | 5.5831 | 5.485 | 5.3759 | 5.2779 | 4.9192 | 4.4567 | 4.3811 | 4.492
| FAIRBOURNE T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 5.2755 | 5.1769 | 5.0271 | 4.628 | 4.2489 | 3.7863 | 3.324 | 2.8178 | 2.2092 | 1.6884 | 1.2605 | 0.058212 | -1.1152 | -1.2893 | -1.1988
| FAZAKERLEY HOSPITAL T1 / JACOBS T1 / JACOBS T2 / SEEDS LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 16.0306 | 17.0243 | 17.1444 | 16.8789 | 16.6324 | 16.3053 | 15.9397 | 15.5605 | 15.2162 | 14.7995 | 14.4142 | 12.7568 | 10.2659 | 9.6765 | 10.0265
| FERODO T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 4.8776 | 4.8958 | 4.7885 | 4.5239 | 4.2205 | 3.8592 | 3.4735 | 3.0546 | 2.5602 | 2.0867 | 1.662 | 0.26829 | -1.4214 | -1.6013 | -1.4516
| FISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.7347 | 4.7972 | 4.7895 | 4.65 | 4.5486 | 4.4268 | 4.3204 | 4.2184 | 4.1408 | 4.0447 | 3.9535 | 3.5264 | 2.8361 | 2.5274 | 2.5258
| FLINT T1 / FLINT T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.949 | 4.2078 | 4.2135 | -0.16327 | -0.41111 | -0.72597 | -1.0396 | -1.3526 | -1.6658 | -2.0039 | -2.3135 | -3.6041 | -5.3566 | -6.0528 | -6.3336
| FODENS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.5 | 2.5828 | 2.5208 | 2.1492 | 1.849 | 1.4748 | 1.1091 | 0.75016 | 0.40167 | 0.024213 | -0.35211 | -1.755 | -3.8688 | -4.934 | -5.2636
| FORD T1 / OXTON T1 / PRENTON LOCAL T1 / SINGLETON AVE T2 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | 12.0204 | 13.2989 | 13.0501 | 11.9446 | 10.7836 | 9.2863 | 7.6852 | 5.835 | 3.8043 | 1.7909 | 0.15601 | -5.9744 | -13.2024 | -19.9421 | -18.6284
| FORDEN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 0.29592 | 1.8416 | 1.9336 | 1.5993 | 1.4805 | 1.2684 | 0.75023 | 0.41433 | 0.035406 | -0.33355 | -0.64189 | -1.6453 | -2.9565 | -3.3019 | -3.1531
| FOUR CROSSES T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.6224 | 1.6781 | 1.6554 | 1.515 | 1.3688 | 1.2087 | 1.0475 | 0.8757 | 0.71171 | 0.53601 | 0.37411 | -0.22266 | -0.97051 | -1.166 | -1.1147
| FRODSHAM LOCAL T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 2.0476 | 2.161 | 1.9112 | 1.2809 | 0.71228 | 0.41984 | -0.76613 | -1.6505 | -2.6423 | -3.5357 | -4.344 | -7.1544 | -10.2599 | -11.4232 | -11.6374
| GADBROOK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.6735 | 3.8137 | 3.7704 | 3.5222 | 3.2573 | 2.9626 | 2.656 | 2.3068 | 1.9361 | 1.5376 | 1.1709 | -0.019425 | -1.862 | -2.4481 | -2.465
| GAERWEN VIEW T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.7653 | 5.7769 | 5.7544 | 5.6158 | 5.495 | 5.336 | 5.1889 | 5.0328 | 4.8697 | 4.6984 | 4.554 | 3.9722 | 3.219 | 3.0673 | 3.0898
| GIGG LA THELWALL T1 / HILLCLIFFE T1 / STOCKTON HEATH T1 / STRETTON IND EST T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 10.2653 | 11.2229 | 11.1441 | 10.111 | 9.0901 | 7.8133 | 6.4825 | 5.096 | 3.6947 | 2.1927 | 0.87493 | -4.1322 | -11.213 | -16.088 | -16.2552
| GILBROOK DOCK T1 / HILL RD T1 / MOBIL OIL (WALLASEY) T1 | 7 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 9.4959 | 10.1533 | 10.211 | 11.7056 | 11.4129 | 11.0367 | 10.6401 | 10.1778 | 9.7531 | 9.3116 | 8.9396 | 7.4088 | 5.7857 | 5.6368 | 5.4678
| GLAN-YR-AFON T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.1735 | 5.2498 | 5.2289 | 5.0787 | 4.9379 | 4.7646 | 4.5959 | 4.4225 | 4.248 | 4.0767 | 3.9375 | 3.4415 | 2.844 | 2.6215 | 2.6571
| GRAIG FAWR T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.2041 | 4.1501 | 3.9381 | 3.3395 | 2.622 | 1.8264 | 0.99785 | 0.096651 | -0.93609 | -1.9336 | -2.827 | -5.6684 | -9.0602 | -9.696 | -9.2728
| GRAVEL T1 / WCB PLASTICS T1 / WHARTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 13.4694 | 13.6663 | 13.6488 | 13.3911 | 13.1401 | 12.8409 | 12.5685 | 12.2809 | 12.0267 | 11.705 | 11.4167 | 10.1403 | 8.2632 | 8.0543 | 8.4474
| GREASBY T1 / SAUGHALL MASSIE T1 / UPTON T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 7.2347 | 7.8035 | 7.666 | 6.8521 | 5.9867 | 4.9214 | 3.7985 | 2.5822 | 1.3212 | 0.044291 | -1.0523 | -5.3759 | -10.775 | -14.5936 | -14.2557
| GREAT SANKEY T1 / PENKETH T1 / WIDNES RD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 9.1837 | 9.4429 | 9.2484 | 8.344 | 7.3636 | 6.187 | 4.9771 | 3.6893 | 2.3533 | 0.99925 | -0.201 | -4.8057 | -10.8394 | -14.9556 | -15.0025
| GREAT SUTTON T1 / LITTLE SUTTON T1 / STRAWBERRY ROUNDABOUT T1 / SUTTON HALL WWB T1 / WHITBY MAIN T2 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 3.42 | 4.7998 | 4.6901 | 3.4785 | 2.1744 | 0.50446 | -1.3018 | -3.2993 | -5.3767 | -7.4856 | -9.3285 | -16.4058 | -25.4427 | -31.5993 | -31.6613
| GREENFIELD T1 / GREENFIELD T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.949 | 4.0461 | 3.9444 | 3.5357 | 3.0881 | 2.5695 | 2.0326 | 1.4676 | 0.86392 | 0.22135 | -0.36888 | -2.5948 | -5.4596 | -5.6704 | -5.2528
| GROSVENOR ST T1 / LINENHALL ST T1 / NORTHGATE TERRACE T1 / STATION VIEW T1 / TOMULAR PLACE T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 8.1429 | 9.5419 | 9.6693 | 9.0377 | 8.6287 | 7.9713 | 7.3364 | 6.7203 | 6.037 | 5.3771 | 4.9367 | 3.0964 | 0.73774 | 0.051508 | 0.74034
| GWERSYLLT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 2.102 | 2.1442 | 1.9867 | 1.9798 | 1.8001 | 2.9869 | -0.58872 | -1.404 | -2.2955 | -3.1813 | -3.9704 | -6.7002 | -9.7496 | -10.0059 | -9.8938
| HALTON RD T1 / MURDISHAW T1 / PERCIVAL LA T4 / RUNCORN CENTRAL T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 6.4796 | 8.2535 | 8.5174 | 8.2946 | 8.1025 | 7.7952 | 7.3402 | 6.8442 | 6.3096 | 5.7094 | 5.2084 | 3.2693 | 0.22355 | -1.4589 | -1.7033
| HARLECH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.1939 | 5.1275 | 5.0106 | 4.6337 | 4.3055 | 3.8902 | 3.4589 | 2.9841 | 2.4415 | 1.9721 | 1.6056 | 0.49236 | -0.6025 | -0.92582 | -0.98303
| HARRINGTON ST T1 / PARADISE ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 3.4041 | 3.6252 | 3.3165 | 3.0136 | 3.0456 | 2.9511 | 2.7818 | 2.5183 | 2.1993 | 1.9496 | 1.6355 | 0.22884 | -1.6426 | -3.3111 | -3.5731
| HARRINGTON ST T2 / HIGHFIELD ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.4653 | 4.5916 | 4.6036 | 4.4684 | 4.3878 | 4.2827 | 4.2094 | 4.157 | 4.1434 | 4.0969 | 4.0429 | 3.6521 | 2.9757 | 2.7839 | 2.9752
| HARRINGTON ST T3 / LIME ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 4.4653 | 4.9486 | 5.0478 | 5.1188 | 5.1227 | 5.1817 | 5.2178 | 5.2499 | 5.2825 | 5.2947 | 5.3262 | 5.3286 | 5.28 | 5.3131 | 5.4895
| HARTFORD T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 1.2449 | 1.6474 | 1.6033 | 1.889 | 2.1322 | 0.84289 | -0.79058 | -1.5764 | -2.4374 | -3.2535 | -3.9292 | -6.2066 | -8.8339 | -10.4137 | -10.9518
| HASKAYNE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 5.3776 | 5.4692 | 5.4471 | 5.3013 | 5.1399 | 4.9439 | 4.7433 | 4.5128 | 4.2582 | 4.023 | 3.8035 | 3.0305 | 2.1459 | 2.0581 | 2.0373
| HATHERTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.8265 | 1.8516 | 1.8222 | 1.7088 | 1.6094 | 1.4865 | 1.3763 | 1.2655 | 1.156 | 1.0389 | 0.92435 | 0.50261 | -0.17381 | -0.34822 | -0.20649
| HERONS WAY T1 / LACHE T1 / MBNA T1 / SMFS KINGSMEADOW T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 19.2041 | 19.6553 | 19.6104 | 19.0386 | 18.4647 | 17.7325 | 16.9965 | 16.2224 | 15.4497 | 14.6373 | 13.936 | 11.1372 | 7.5873 | 5.4071 | 5.7565
| HIGHFIELD ST T2 / LIME ST T2 / OLD HAYMARKET T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 10.7505 | 11.0011 | 10.9779 | 10.7549 | 10.6073 | 10.4178 | 10.234 | 10.0493 | 9.8576 | 9.6585 | 9.4217 | 8.4518 | 6.8998 | 6.5903 | 6.9693
| HOLMES CHAPEL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.6939 | 1.7961 | 1.7176 | 1.3085 | 0.89914 | 0.69936 | -0.067808 | -0.55557 | -1.0816 | -1.5933 | -2.0217 | -3.5873 | -5.7194 | -6.9501 | -6.9362
| HOLT LA (WARRINGTON RD) T1 / PRESCOT T1 / RAINHILL LOCAL T1 / WHISTON HOSP T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 10.1735 | 11.6774 | 11.7317 | 11.12 | 10.4547 | 9.5119 | 8.461 | 7.2506 | 5.9697 | 4.6026 | 3.4439 | -1.1 | -6.3351 | -9.7711 | -8.7089
| HOLWAY RD T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 3.2143 | 3.3271 | 3.2769 | 2.9568 | 2.6647 | 2.3021 | 1.951 | 1.5902 | 1.2141 | 0.85341 | 0.57744 | -0.50949 | -1.7409 | -2.3499 | -2.3092
| HOLYHEAD T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 4.8061 | 4.8366 | 4.7585 | 4.5343 | 4.2481 | 3.9395 | 3.6131 | 3.2331 | 2.7852 | 2.3611 | 1.9589 | 0.82608 | -0.8773 | -1.1117 | -0.87576
| HOLYWELL T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.3469 | 3.4052 | 3.3008 | 2.888 | 2.4091 | 1.8704 | 1.3014 | 0.65661 | -0.0096952 | -0.66275 | -1.2273 | -3.1466 | -5.5266 | -6.2292 | -6.3052
| HOOTON MAIN T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 2.8878 | 2.8793 | 2.7622 | 2.2713 | 1.7665 | 1.1822 | 0.5825 | -0.072616 | -0.71853 | -1.3464 | -1.9209 | -4.1054 | -6.7153 | -7.7836 | -8.0498
| HUNTS CROSS T1 / KENTON RD T1 / WOODEND AVE T1 / WOOLTON T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 13.0102 | 13.8284 | 13.6495 | 12.6132 | 11.5036 | 10.1012 | 8.6259 | 7.0184 | 5.3413 | 3.6203 | 2.126 | -3.7644 | -11.3166 | -16.9679 | -16.2835
| HUYTON HEY RD T1 / WILSON RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 2.9694 | 3.2672 | 3.2205 | 2.7804 | 2.3231 | 1.7454 | 1.1695 | 0.55642 | -0.085735 | -0.7228 | -1.2568 | -3.3402 | -5.9086 | -7.5078 | -7.4282
| IFTON T1 / IFTON T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.9592 | 4.1082 | 4.0378 | 3.6025 | 3.1433 | 2.6007 | 2.0421 | 1.4412 | 0.82389 | 0.20747 | -0.34061 | -2.4522 | -5.1165 | -6.4712 | -6.352
| ILFORDS T1 / KNUTSFORD T1 / MOBBERLEY T1 / RADBROKE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 15.2857 | 15.7468 | 15.6449 | 14.9656 | 14.2285 | 13.3849 | 12.5377 | 11.6132 | 10.6889 | 9.6846 | 8.7531 | 5.2651 | 0.43448 | -0.36598 | 0.22173
| IVY ST (SOUTHPORT) T1 / KENSINGTON RD T1 / MARKET ST T1 / SOUTHPORT T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 14.6633 | 15.2202 | 15.2078 | 14.565 | 13.9364 | 13.2025 | 12.5086 | 11.8063 | 11.1261 | 10.3777 | 9.7097 | 7.032 | 3.1392 | 2.2673 | 2.7482
| IVY ST T1 / LLYSFAEN RD T1 / OLD MILL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 7.9184 | 8.6394 | 8.5328 | 7.7545 | 6.9483 | 5.9013 | 4.8128 | 3.6041 | 2.2723 | 1.0111 | 0.029116 | -3.5215 | -7.4663 | -10.3461 | -10.072
| JOHNSTOWN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.0816 | 1.0993 | 0.92752 | 0.73593 | 0.07496 | -0.54017 | -1.6002 | -2.377 | -3.2223 | -4.0785 | -4.8679 | -7.6101 | -10.9194 | -10.6831 | -10.0828
| KELCO T1 / NEWS INTERNATIONAL T1 / NEWS INTERNATIONAL T2 / PALCO T1 / SOUTHDENE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 12.4286 | 13.0134 | 13.0708 | 22.4884 | 22.0966 | 21.5937 | 21.1738 | 20.8695 | 20.7081 | 20.4031 | 20.1001 | 18.1087 | 14.8867 | 13.8972 | 14.5231
| KINGSLAND 33 T1 / SAFEWAY T1 / WOOLSTON T1 / WOOLSTON T2 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 12.7857 | 14.1303 | 14.301 | 13.96 | 13.6343 | 13.1573 | 12.6145 | 12.0469 | 11.483 | 10.8482 | 10.3048 | 6.5745 | 1.8479 | 1.87 | 2.813
| KINNERTON T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 4.1939 | 4.1197 | 3.9927 | 3.6635 | 3.2476 | 2.818 | 2.3704 | 1.857 | 1.2943 | 0.73849 | 0.20257 | -1.2997 | -3.4215 | -3.8836 | -3.5434
| KIRKBY CENTRAL T1 / NORTHWOOD T1 / TOWER HILL (BANK LA) T1 / WESTVALE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 11.7857 | 13.2484 | 13.2366 | 12.6289 | 11.8892 | 10.8377 | 9.6878 | 8.3785 | 6.9445 | 5.5132 | 4.3427 | -0.39506 | -5.9718 | -10.7183 | -9.2762
| KNOWSLEY T1 / MARLED HEY T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 5.6531 | 5.8885 | 5.9023 | 5.7065 | 5.5426 | 5.3366 | 5.1127 | 4.8835 | 4.6671 | 4.4333 | 4.21 | 3.3322 | 2.1418 | 1.6912 | 1.5387
| KNUTSFORD T2 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 1.9417 | 2.124 | 2.078 | 1.8076 | 1.5179 | 1.1807 | 0.84313 | 0.42114 | 0.045577 | -0.33876 | -0.6842 | -1.9375 | -3.5891 | -4.113 | -4.049
| LCWW HUNTINGTON T1 / LCWW HUNTINGTON T2 | 7 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.549 | 4.7064 | 4.6952 | 4.4947 | 4.3209 | 4.0973 | 3.8876 | 3.6742 | 3.4677 | 3.2496 | 3.0527 | 2.1881 | 0.91572 | 0.2554 | 0.46684
| LEA GREEN T1 / PILKINGTONS HO T1 / RAVENHEAD RETAIL PK T1 / SOMERFIELD DISTRIBUTION T1 | 11 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 7.1327 | 8.1623 | 8.2944 | 8.012 | 7.7663 | 7.4062 | 7.0023 | 6.5736 | 6.1521 | 5.6524 | 5.2233 | 3.511 | 0.86946 | -0.38889 | -0.62467
| LEGACY LOCAL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.2041 | 5.4018 | 5.401 | 5.3041 | 5.1585 | 4.9699 | 4.756 | 4.4994 | 4.2226 | 3.9629 | 3.7372 | 3.0199 | 2.3777 | 2.3924 | 2.4455
| LEIGHTON HOSP T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.9796 | 4.2742 | 4.2948 | 4.2551 | 4.1751 | 4.0965 | 3.9866 | 3.8464 | 3.6976 | 3.5643 | 3.4655 | 2.913 | 1.9983 | 1.9159 | 2.2283
| LIVERPOOL RD 33 T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 6.9592 | 7.1109 | 7.041 | 6.7472 | 6.4374 | 6.0445 | 5.6527 | 5.2198 | 4.7204 | 4.2511 | 3.8739 | 2.5711 | 1.2079 | 1.3261 | 1.6187
| LLAINGOCH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 4.3061 | 4.4235 | 4.2558 | 3.8948 | 3.406 | 2.8126 | 2.179 | 1.4329 | 0.53272 | -0.33467 | -1.0943 | -3.3103 | -5.566 | -5.1762 | -4.6063
| LLANARMON T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 5.9286 | 5.9924 | 5.9777 | 5.8978 | 5.7964 | 5.6869 | 5.564 | 5.4371 | 5.3066 | 5.1709 | 5.0573 | 4.6446 | 4.0093 | 3.5959 | 3.5728
| LLANBEDROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 1.9694 | 1.9731 | 1.9097 | 1.6592 | 1.3948 | 1.0787 | 0.77928 | 0.43718 | 0.047111 | -0.29365 | -0.57243 | -1.3894 | -2.1758 | -2.2183 | -2.1963
| LLANBERIS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 1.4592 | 1.5969 | 1.5601 | 1.3019 | 1.0456 | 0.71361 | 0.39187 | 0.040915 | -0.35943 | -0.73544 | -1.0137 | -1.9272 | -2.8554 | -2.8818 | -2.6774
| LLANDDEUSANT T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.7653 | 3.8774 | 3.7941 | 3.5304 | 3.2008 | 2.8369 | 2.4349 | 1.9679 | 1.431 | 0.91365 | 0.45224 | -0.90402 | -2.4406 | -2.6834 | -2.315
| LLANDDU QUARRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 0.52041 | 0.69751 | 0.70447 | 0.56024 | 0.41437 | 0.23592 | 0.051503 | -0.14483 | -0.33794 | -0.53761 | -0.7249 | -1.4359 | -2.4314 | -2.901 | -2.8524
| LLANDEGFAN T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.0204 | 5.1065 | 5.0737 | 4.9141 | 4.7121 | 4.4855 | 4.2356 | 3.9547 | 3.6545 | 3.3689 | 3.1145 | 2.1975 | 0.95407 | 0.10406 | 0.16779
| LLANDRINIO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.5353 | 2.5496 | 2.4931 | 2.4125 | 2.3248 | 2.0628 | 1.4954 | 1.2056 | 0.90242 | 0.60556 | 0.33896 | -0.62359 | -1.9631 | -2.4635 | -2.4889
| LLANDUDNO T1 / LLANDUDNO T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.8878 | 4.2896 | 4.266 | 4.0092 | 3.7033 | 3.3406 | 2.9535 | 2.5086 | 1.9766 | 1.4622 | 1.0428 | -0.12705 | -1.8434 | -2.2695 | -2.0268
| LLANDYFRYDOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.1531 | 5.2052 | 5.1601 | 4.9381 | 4.7199 | 4.44 | 4.1634 | 3.8769 | 3.5399 | 3.2449 | 3.0014 | 2.2426 | 1.2985 | 0.76457 | 0.7131
| LLANDYRNOG T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 1.9184 | 2.0786 | 2.0768 | 1.9528 | 1.8237 | 1.6687 | 1.5006 | 1.3313 | 1.1554 | 0.9694 | 0.81701 | 0.20731 | -0.7181 | -1.2561 | -1.1813
| LLANFAELOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 1.2857 | 1.3553 | 1.3318 | 1.1978 | 1.0609 | 0.89085 | 0.72188 | 0.55379 | 0.37814 | 0.20413 | 0.062721 | -0.46681 | -1.1198 | -1.143 | -0.80796
| LLANFAIR CAEREINION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.4388 | 2.539 | 2.4178 | 1.996 | 1.5164 | 0.97591 | 0.41737 | -0.20657 | -0.89775 | -1.5467 | -2.0843 | -3.7624 | -5.6874 | -6.2042 | -5.9999
| LLANFAIR PG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.3571 | 3.4995 | 3.4128 | 3.0821 | 2.7009 | 2.2446 | 1.7696 | 1.2348 | 0.59951 | -0.00039513 | -0.50036 | -1.979 | -3.255 | -3.154 | -2.7629
| LLANFAIRFECHAN T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 5.4082 | 5.4359 | 5.3761 | 5.1211 | 4.8611 | 4.5302 | 4.222 | 3.8849 | 3.471 | 3.1126 | 2.8469 | 2.0082 | 1.2436 | 0.74037 | 0.8075
| LLANFROTHEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.4082 | 5.3748 | 5.2937 | 4.983 | 4.6445 | 4.2543 | 3.8641 | 3.43 | 2.9435 | 2.5086 | 2.1537 | 0.99691 | -0.18311 | -0.23634 | -0.26641
| LLANFWROG T1 / RUTHIN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 5.7959 | 6.2057 | 6.1404 | 5.6203 | 5.0562 | 4.3797 | 3.672 | 2.9134 | 1.8985 | 1.0793 | 0.13811 | -3.1119 | -7.2152 | -7.4563 | -7.0457
| LLANFYLLIN T1 / LLANFYLLIN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.5449 | 2.7899 | 4.9406 | 4.4972 | 4.0596 | 3.4994 | 2.9394 | 2.3393 | 1.6199 | 0.99457 | 0.56489 | -0.82288 | -2.1774 | -2.8934 | -2.9747
| LLANGAFFO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.8061 | 3.8838 | 3.8441 | 3.62 | 3.3843 | 3.0873 | 2.7997 | 2.4744 | 2.1555 | 1.8198 | 1.5247 | 0.39466 | -1.1771 | -2.1465 | -1.9803
| LLANGEFNI IND EST T1 / LLANGEFNI IND EST T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5204 | 3.7304 | 3.7426 | 3.5281 | 3.3645 | 3.1633 | 2.9801 | 2.8347 | 2.741 | 2.5896 | 2.4409 | 1.6093 | 0.26814 | -0.15208 | 0.12672
| LLANGEFNI T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.5612 | 3.6588 | 3.6039 | 3.2994 | 2.9884 | 2.6009 | 2.2107 | 1.7974 | 1.3634 | 0.9289 | 0.56452 | -0.80936 | -2.3244 | -2.6237 | -2.5722
| LLANGOLLEN T1 / LLANGOLLEN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.0918 | 5.2705 | 5.2189 | 4.8456 | 4.4551 | 3.9704 | 3.477 | 2.9529 | 2.3551 | 1.804 | 1.406 | 0.034219 | -1.4702 | -2.3859 | -2.163
| LLANIDLOES T1 / LLANIDLOES T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.3729 | 1.5099 | 1.3895 | 0.81539 | 0.49078 | 0.099735 | -1.2418 | -2.0356 | -3.0609 | -3.9298 | -4.5482 | -6.3167 | -7.8708 | -7.7971 | -7.9925
| LLANILAR T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 0.78163 | 0.79526 | 0.72993 | 0.50376 | 0.52764 | 0.60092 | -0.38805 | -0.73758 | -1.1141 | -1.48 | -1.8027 | -2.8126 | -3.9781 | -4.2441 | -4.1522
| LLANRWST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 3.9592 | 4.1514 | 4.1244 | 3.8808 | 3.629 | 3.3042 | 2.9717 | 2.6054 | 2.1816 | 1.8054 | 1.5309 | 0.61493 | -0.28919 | -0.82798 | -0.62737
| LLANSANNAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 4.7449 | 4.7652 | 4.6874 | 4.3878 | 4.0602 | 3.6828 | 3.2969 | 2.8837 | 2.3853 | 1.9573 | 1.6351 | 0.8246 | -0.0089489 | -0.1831 | 0.0086211
| LLANSILIN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.9898 | 4.079 | 4.0005 | 3.6931 | 3.3331 | 2.9192 | 2.5003 | 2.0333 | 1.4966 | 1.0106 | 0.60859 | -0.51387 | -1.7837 | -2.1356 | -2.0105
| LLYNCLYS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.3265 | 3.2743 | 3.148 | 2.7846 | 2.3294 | 1.847 | 1.3664 | 0.81259 | 0.21617 | -0.37455 | -0.92826 | -2.494 | -4.8294 | -5.377 | -5.0731
| LORD ST T1 / MARSHSIDE T1 / MULLARDS BALMORAL DV T1 / SOUTHPORT T2 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 11.949 | 13.0816 | 12.7752 | 11.282 | 9.4844 | 7.2756 | 4.8902 | 2.1342 | -0.81218 | -3.6641 | -6.0974 | -15.0044 | -25.1868 | -32.3126 | -32.4963
| LOSTOCK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 3.1531 | 3.2531 | 3.1599 | 2.8325 | 2.4486 | 2.0187 | 1.5519 | 1.0502 | 0.50457 | -0.043676 | -0.54078 | -2.2989 | -4.6302 | -5.4385 | -5.3712
| LOSTOCK TRIANGLE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.6327 | 4.6082 | 4.5319 | 4.3752 | 4.1352 | 3.8956 | 3.6681 | 3.3804 | 3.0679 | 2.7248 | 2.3956 | 1.3993 | -0.32277 | -0.722 | -0.43269
| LOWER BEBINGTON T1 / NEW FERRY T1 / SPITAL T1 / UNILEVER RESEARCH T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | 15.2245 | 15.578 | 15.1898 | 13.8557 | 12.4759 | 10.7739 | 8.9894 | 7.0039 | 4.8627 | 2.7585 | 0.91861 | -5.8348 | -13.37 | -18.0547 | -17.5643
| LUGSDALE T1 / PILK SULLIVAN T1 / PILK SULLIVAN T2 / USAC T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 20.398 | 20.7082 | 20.7265 | 20.3428 | 20.1276 | 19.8324 | 19.5837 | 19.4223 | 19.3414 | 19.1968 | 19.062 | 18.0888 | 16.5826 | 16.3732 | 16.9064
| LYMM T1 / WHITELEGGS LA T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 0.94898 | 2.7775 | 2.6139 | 2.5366 | 1.0844 | 0.38418 | -0.97863 | -2.183 | -3.5291 | -4.8628 | -6.0591 | -9.9245 | -14.5589 | -14.6521 | -14.307
| MACHYNLLETH T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 1.4082 | 1.4051 | 1.3011 | 0.97099 | 0.60457 | 0.16304 | -0.28939 | -0.80448 | -1.4345 | -1.9901 | -2.4282 | -3.7829 | -5.0855 | -4.6963 | -4.328
| MACHYNLLETH T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.3773 | 2.385 | 2.3138 | 2.0402 | 1.7459 | 1.3952 | 1.0445 | 0.6555 | 0.20301 | -0.20378 | -0.53035 | -1.5084 | -2.5129 | -2.6476 | -2.5482
| MAELOR CREAMERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.0612 | 4.22 | 4.2276 | 4.1165 | 4.0279 | 3.9283 | 3.8225 | 3.7418 | 3.6648 | 3.5662 | 3.4836 | 3.0745 | 2.4513 | 2.2973 | 2.4667
| MAENTWROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.9082 | 5.8864 | 5.8215 | 5.6247 | 5.4343 | 5.2039 | 4.9586 | 4.7019 | 4.4183 | 4.1564 | 3.9286 | 3.148 | 2.3173 | 2.218 | 2.1803
| MAES-Y-CLAWDD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.8163 | 2.966 | 2.9386 | 2.7159 | 2.4877 | 2.2458 | 2.0123 | 1.5743 | 1.1152 | 0.60698 | 0.071728 | -1.7207 | -4.3813 | -5.0384 | -4.8671
| MANOD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.8571 | 2.806 | 2.7449 | 2.5509 | 2.3519 | 2.1066 | 1.8659 | 1.605 | 1.2955 | 1.0176 | 0.79668 | 0.24017 | -0.36102 | -0.31846 | -0.20409
| MANOR PK T1 / NORTON CHAINS T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 0.84694 | 2.2613 | 1.7145 | 0.85592 | 0.46004 | 0.019104 | -0.54956 | -1.2445 | -2.0393 | -2.6413 | -3.4155 | -6.8693 | -11.5204 | -14.9565 | -15.6045
| MDHB EGERTON DOCK T1 / MDHB EGERTON DOCK T2 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | 3.5485 | 3.9529 | 3.8463 | 3.2748 | 3.5325 | 2.7952 | 2.0398 | 1.173 | 0.2495 | -0.69118 | -1.5229 | -4.6176 | -8.6538 | -10.9099 | -10.4576
| MERE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.7653 | 2.739 | 2.5565 | 1.9574 | 2.1247 | 2.6859 | -0.31938 | -1.2186 | -2.1818 | -3.1046 | -3.9009 | -6.6686 | -9.7826 | -10.4533 | -10.9009
| MERES EDGE T1 / MERES EDGE T2 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 5.4694 | 5.496 | 5.3421 | 4.8738 | 4.3145 | 3.6676 | 3.0078 | 2.2609 | 1.3994 | 0.58196 | -0.13925 | -2.4764 | -5.1953 | -5.5807 | -5.4371
| MIDDLEWICH T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.7653 | 3.7444 | 3.7998 | 5.0976 | 4.5143 | 4.05 | 3.5996 | 2.4354 | 1.9132 | 1.4123 | 0.98624 | -0.60121 | -2.4267 | -3.334 | -3.266
| MIDPOINT POCHIN WAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 5.7755 | 5.8271 | 5.8198 | 5.7591 | 5.7153 | 5.6554 | 5.6008 | 5.5568 | 5.5262 | 5.4775 | 5.4344 | 5.2036 | 4.8091 | 4.6803 | 4.7415
| MILFORD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 2.9388 | 3.1109 | 3.0563 | 2.7611 | 2.4508 | 2.0771 | 1.7217 | 1.3021 | 0.83207 | 0.39645 | 0.016126 | -1.1817 | -2.7972 | -3.1355 | -3.045
| MINFFORDD T1 / PARC BRYN CEGIN T1 / PARC BRYN CEGIN T2 | 11 | BANGOR GT2 / CAERNARFON GT2 | 16.3265 | 16.4272 | 16.3714 | 16.1118 | 15.8373 | 15.479 | 15.1153 | 14.7495 | 14.3265 | 13.9223 | 13.594 | 12.316 | 10.9662 | 10.201 | 10.6465
| MOCHDRE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.7857 | 3.9192 | 3.9121 | 3.7598 | 3.6316 | 3.4729 | 3.329 | 3.2005 | 3.0789 | 2.934 | 2.8073 | 2.2119 | 1.3998 | 1.1667 | 1.1813
| MONA T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 5.7347 | 5.7474 | 5.7149 | 5.5689 | 5.4141 | 5.2315 | 5.0401 | 4.8401 | 4.6256 | 4.4054 | 4.2269 | 3.5383 | 2.6405 | 2.3069 | 2.2666
| MONSANTO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 5.9898 | 5.9721 | 5.8934 | 5.6381 | 5.3869 | 5.0661 | 4.76 | 4.415 | 3.9946 | 3.643 | 3.3673 | 2.4646 | 1.6199 | 1.2007 | 1.0921
| MORDA T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 4.102 | 4.0768 | 3.9461 | 3.6105 | 3.1497 | 2.6493 | 2.1226 | 1.5064 | 0.83057 | 0.14667 | -0.49752 | -2.4734 | -4.553 | -4.5787 | -4.1863
| MORGANITE CERAMICS T1 / PLYMYARD T2 / VAUXHALL NORTH RD T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 13.102 | 13.1901 | 13.0364 | 12.4282 | 11.779 | 10.9936 | 10.1934 | 9.3093 | 8.394 | 7.4519 | 6.5798 | 3.2635 | -0.70197 | -1.4811 | -1.4263
| MORRISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 2.0816 | 2.2375 | 2.2175 | 1.973 | 1.7515 | 1.493 | 1.2526 | 1.0072 | 0.7995 | 0.56807 | 0.33837 | -0.63258 | -1.9311 | -2.2434 | -2.1257
| NANTWICH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.8163 | 1.9205 | 1.7869 | 1.3665 | 1.5895 | 2.0977 | 0.099692 | -0.4199 | -0.98302 | -1.5339 | -2.086 | -3.8802 | -6.6346 | -7.7479 | -7.7862
| NANT-Y-GAMAR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 2.6531 | 2.8058 | 2.7511 | 2.4036 | 2.0555 | 1.7427 | 1.2137 | 0.78055 | 0.32906 | -0.1188 | -0.51188 | -2.0095 | -3.9222 | -5.051 | -5.0538
| NEVILL ST T1 / OCEAN PLAZA T1 / YORK RD T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 9.551 | 9.8522 | 9.8542 | 9.3879 | 9.0373 | 8.5836 | 8.1941 | 7.8561 | 7.5773 | 7.249 | 6.9688 | 5.543 | 3.4988 | 2.8874 | 3.1496
| NEW BRIGHTON T1 / SEAVIEW RD T2 / WALLASEY T1 / WALLASEY VILLAGE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 15.449 | 16.6247 | 16.6192 | 15.7944 | 14.9738 | 13.9188 | 12.7891 | 11.5246 | 10.0829 | 8.7341 | 7.7128 | 4.5741 | 0.89127 | -1.0162 | -2.2225
| NEWHALL T1 / NEWHALL T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 6 | 6.1099 | 6.1081 | 5.9419 | 5.8132 | 5.6635 | 5.5139 | 5.3821 | 5.2731 | 5.1359 | 5.0104 | 4.3832 | 3.4164 | 3.1091 | 3.2731
| NORTH WALES PAPER T1 / NORTH WALES PAPER T2 / WOODFIELD AVE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 7.398 | 7.8353 | 7.8084 | 7.2842 | 6.8475 | 6.292 | 5.7668 | 5.277 | 4.8425 | 4.3249 | 3.8764 | 1.7028 | -1.4503 | -3.2309 | -2.5723
| NORTH WEST WATER CAMPUS T1 / NORTH WEST WATER CAMPUS T2 / OMEGA T1 / OMEGA T2 / ORION BOULEVARD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 24.8776 | 25.8151 | 25.9286 | 25.5969 | 25.3581 | 25.0204 | 24.6744 | 24.1664 | 23.9043 | 23.5508 | 23.2583 | 21.7783 | 19.7665 | 19.5786 | 20.3852
| OPTICAL FIBRES T1 / SHOTWICK T1 / WALBRO T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 7.2041 | 7.5749 | 7.6106 | 7.1862 | 6.9081 | 6.5655 | 6.2893 | 6.121 | 6.0688 | 5.8942 | 5.726 | 4.4297 | 2.1841 | 1.5926 | 2.2287
| ORB CL T1 / STONEBRIDGE LA T1 / STONEBRIDGE LA T2 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 10.8163 | 11.1139 | 11.1099 | 10.7114 | 10.3979 | 10.0024 | 9.638 | 9.3072 | 9.0369 | 8.7041 | 8.3926 | 6.8645 | 4.5629 | 3.7282 | 3.7734
| ORFORD T1 / PADGATE T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 1.051 | 4.8144 | 4.6841 | 2.4431 | 1.2417 | -0.34638 | -2.1365 | -4.2834 | -6.7848 | -9.0396 | -11.2031 | -19.1524 | -28.0754 | -35.7664 | -35.6642
| OTIS ELEVATOR T1 / ST IVEL FOODS T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 5.0306 | 5.1721 | 5.1895 | 5.0198 | 4.9123 | 4.7789 | 4.6699 | 4.5992 | 4.5803 | 4.5136 | 4.4471 | 3.9353 | 3.0862 | 2.8806 | 3.1437
| OVERTON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.8571 | 3.8593 | 3.7382 | 3.1674 | 2.6607 | 2.0051 | 1.3935 | 0.74037 | -0.080392 | -0.74086 | -1.1195 | -2.0209 | -2.3955 | -2.2771 | -2.2435
| PANDY T1 / PANDY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 1.7143 | 2.3587 | 2.3953 | 2.0748 | 1.7584 | 1.3356 | 0.8641 | 0.32734 | -0.26087 | -0.84454 | -1.3919 | -3.3162 | -5.9638 | -7.1337 | -7.7197
| PARC CYBI T1 / PARC CYBI T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 7.0816 | 7.108 | 7.0538 | 6.8172 | 6.5872 | 6.3222 | 6.072 | 5.8142 | 5.5295 | 5.2766 | 5.0573 | 4.3097 | 3.3472 | 3.0594 | 3.058
| PARC MENAI T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 5.9898 | 5.9998 | 5.9537 | 5.8405 | 5.7037 | 5.548 | 5.3779 | 5.2007 | 4.9889 | 4.778 | 4.5725 | 3.9979 | 3.2203 | 3.1735 | 3.3702
| PEBLIC MILLS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 6.398 | 6.356 | 6.3011 | 6.1705 | 5.8838 | 5.6941 | 5.4992 | 5.0946 | 4.5975 | 4.0855 | 3.5914 | 2.2796 | 0.36165 | -0.10574 | 0.13239
| PENMAENMAWR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 5.1429 | 5.1374 | 5.0346 | 4.6674 | 4.2887 | 3.824 | 3.3648 | 2.8438 | 2.2144 | 1.6645 | 1.2198 | -0.12288 | -1.4466 | -1.3679 | -1.2781
| PENTRAETH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | 3.0612 | 3.1907 | 3.1394 | 2.7643 | 2.4093 | 1.962 | 1.5374 | 1.0706 | 0.57846 | 0.12211 | -0.23482 | -1.5123 | -3.0564 | -3.87 | -4.0896
| PEN-Y-GROES T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 2.3122 | 2.3007 | 2.2235 | 1.8931 | 1.5482 | 1.139 | 0.73486 | 0.31386 | -0.18145 | -0.6246 | -0.95127 | -2.0363 | -3.5427 | -4.2332 | -4.0977
| PILKINGTONS T1 / PILKINGTONS T2 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 6.4592 | 6.6158 | 6.6169 | 6.4647 | 6.3261 | 6.1457 | 5.9594 | 5.777 | 5.5988 | 5.3974 | 5.2523 | 4.6415 | 3.7698 | 3.2906 | 3.4281
| POINT OF AYR COLLIERY T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 2.2755 | 2.3799 | 2.3202 | 2.0064 | 1.6728 | 1.2787 | 0.8944 | 0.51008 | 0.076523 | -0.34807 | -0.71547 | -2.0163 | -3.6288 | -3.8724 | -3.5674
| PORTHMADOG T1 / PORTHMADOG T2 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 5.6633 | 5.7504 | 5.6373 | 5.1904 | 4.6986 | 4.0936 | 3.4852 | 2.8139 | 2.0172 | 1.2988 | 0.73756 | -1.0124 | -2.8466 | -2.5663 | -2.3372
| PREES T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 2.1633 | 2.5128 | 2.5035 | 2.3064 | 2.04 | 1.7325 | 1.3753 | 0.98269 | 0.51863 | 0.090588 | -0.28929 | -1.3954 | -2.7481 | -3.01 | -2.7271
| PRIMROSE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 4.8265 | 4.8937 | 4.8823 | 4.7361 | 4.6048 | 4.4457 | 4.3015 | 4.1552 | 4.0184 | 3.8772 | 3.7379 | 3.1827 | 2.433 | 2.2022 | 2.1733
| PWLLHELI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 3.8673 | 4.0295 | 3.9954 | 3.7345 | 3.4737 | 3.1349 | 2.7978 | 2.4387 | 2.0384 | 1.6713 | 1.4014 | 0.44895 | -0.46288 | -1.0347 | -0.91243
| RADWAY GREEN T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.3469 | 1.5352 | 1.4754 | 1.0728 | 1.3414 | 1.5869 | -0.26602 | -0.75672 | -1.2417 | -1.7422 | -2.1811 | -3.872 | -6.1368 | -7.5535 | -7.6336
| RAVEN SQUARE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 1.0102 | 1.2409 | 1.1853 | 0.77853 | 0.39025 | 0.44932 | -0.60527 | -1.1274 | -1.708 | -2.2619 | -2.7494 | -4.5619 | -6.5183 | -6.6931 | -6.5687
| REFORM ST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 2.7551 | 3.0084 | 2.9608 | 2.6967 | 2.5122 | 2.2578 | 2.0011 | 1.7096 | 1.3542 | 1.0324 | 0.79028 | 0.033019 | -0.90688 | -1.3478 | -1.2063
| RHM FOODS LTD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 6.2347 | 6.2716 | 6.2738 | 6.2262 | 6.1993 | 6.1648 | 6.1383 | 6.1181 | 6.1073 | 6.092 | 6.0766 | 5.9448 | 5.7317 | 5.6721 | 5.7279
| RHOSLAN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 4.2143 | 4.2126 | 4.0861 | 3.6609 | 3.1593 | 2.5926 | 2.0136 | 1.3341 | 0.57327 | -0.11898 | -0.71924 | -2.4491 | -4.0631 | -4.121 | -4.0095
| RHUDDLAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.2857 | 3.5643 | 3.5242 | 3.3018 | 2.9986 | 2.6454 | 2.2563 | 1.8054 | 1.2917 | 0.79285 | 0.36694 | -0.95062 | -2.3272 | -2.3058 | -2.1652
| RHYDLYDAN T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 2.9286 | 2.9241 | 2.8684 | 2.7302 | 2.5342 | 2.3302 | 2.1096 | 1.8608 | 1.5622 | 1.297 | 1.0805 | 0.51053 | -0.19642 | -0.31142 | -0.24846
| RHYD-Y-FOEL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 4.9184 | 4.8447 | 4.7315 | 4.4105 | 4.0448 | 3.6303 | 3.2215 | 2.6963 | 2.1715 | 1.6874 | 1.2697 | 0.11902 | -1.225 | -1.3633 | -1.0528
| RINGWAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | -0.046939 | 6.5729 | 6.5244 | 6.3153 | 6.0249 | 5.7081 | 5.3571 | 4.9399 | 4.4828 | 4.0491 | 3.6504 | 2.5328 | 1.3751 | 1.3521 | 1.3865
| RIVALS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.6224 | 2.5546 | 2.4613 | 2.2463 | 3.1868 | 2.8991 | 2.6142 | 2.2853 | 1.8785 | 1.5326 | 1.2218 | 0.47472 | -0.33947 | -0.41432 | -0.21909
| ROLLS ROYCE T1 / ROLLS ROYCE T2 / ROLLS ROYCE T3 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.1224 | 4.0453 | 4.1504 | 3.9611 | 3.8229 | 3.6197 | 3.3806 | 2.9285 | 2.4132 | 1.852 | 1.2798 | -0.71206 | -3.8407 | -4.8538 | -4.5667
| ROSSETT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 4.2245 | 3.4955 | 2.5606 | 1.7408 | 0.79789 | 0.047835 | -0.89748 | -2.0888 | -3.5626 | -4.6144 | -5.9054 | -10.212 | -15.6556 | -19.1978 | -20.0551
| ROYAL INSURANCE (NEW QUAY) T1 / ROYAL INSURANCE (NEW QUAY) T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 8.2612 | 8.1596 | 8.0576 | 7.9146 | 7.7214 | 7.4994 | 7.2599 | 6.9429 | 6.5667 | 6.1928 | 5.8102 | 4.8733 | 3.2564 | 3.0462 | 3.3538
| RUABON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.1837 | 3.3884 | 3.2887 | 2.8534 | 2.4235 | 1.8799 | 1.3298 | 0.74812 | 0.14916 | -0.4548 | -0.97585 | -3.102 | -5.7637 | -7.6946 | -7.3379
| SALTNEY T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.9388 | 4.9588 | 4.9197 | 4.7642 | 4.5994 | 4.4138 | 4.2303 | 4.0305 | 3.8121 | 3.5863 | 3.3817 | 2.6521 | 1.6198 | 1.4752 | 1.7258
| SANDBACH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | -0.16327 | 1.1929 | 9.4939 | 9.9287 | 6.8251 | 6.3025 | 5.7871 | 5.2506 | 4.6923 | 4.1414 | 3.6756 | 1.8747 | -0.42674 | -1.7919 | -1.7367
| SHAWBURY T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.4601 | 1.5243 | 1.4446 | 1.096 | 0.71418 | 0.30816 | -0.099467 | -0.70453 | -1.3689 | -2.0599 | -2.7407 | -5.0207 | -7.9945 | -8.8926 | -8.6977
| SMALLWOOD T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.7653 | 1.7309 | 1.426 | 1.8887 | 1.7195 | 0.69786 | -1.307 | -2.2398 | -3.2843 | -4.2345 | -5.185 | -8.3074 | -11.954 | -13.065 | -12.8291
| SNOWHILL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 1.9184 | 2.0547 | 1.9583 | 1.5725 | 1.1731 | 0.70773 | 0.25986 | -0.24514 | -0.81155 | -1.3779 | -1.8757 | -3.3996 | -5.7026 | -6.4695 | -6.3611
| ST ASAPH BUSINESS PK T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 2.9997 | 2.8487 | 2.6506 | 2.2166 | 1.899 | 1.435 | 0.97076 | 0.3785 | -0.54241 | -1.3424 | -2.0008 | -4.0637 | -5.657 | -6.4632 | -4.9553
| ST HELENS RD T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 3.2245 | 3.3578 | 3.3204 | 3.0579 | 2.7989 | 2.466 | 2.1497 | 1.8146 | 1.4505 | 1.0877 | 0.80699 | -0.2886 | -1.4836 | -2.1095 | -1.7211
| STAPELEY T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4592 | 2.5021 | 2.2249 | 1.6816 | 1.3712 | 0.93874 | 0.44282 | -0.14633 | -0.8047 | -1.3383 | -1.9483 | -4.2837 | -7.2922 | -9.4997 | -9.9496
| TACO PLASTICS T1 / TACO PLASTICS T2 / UNITED PERIPHERALS T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 8.9082 | 9.155 | 9.1149 | 8.4651 | 8.1109 | 7.6125 | 7.1637 | 6.8487 | 6.59 | 6.2703 | 6.0177 | 4.7603 | 3.059 | 3.3227 | 4.2331
| TARPORLEY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 3.2959 | 3.4298 | 3.3601 | 3.0451 | 2.674 | 2.2487 | 1.8041 | 1.2899 | 0.74854 | 0.22462 | -0.2436 | -1.8002 | -3.7229 | -4.1279 | -4.1304
| TARVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 1.5204 | 1.7747 | 1.7215 | 1.3995 | 1.3597 | 1.8868 | -0.21384 | -0.84537 | -1.4991 | -2.1609 | -2.7351 | -4.8094 | -7.5998 | -9.2583 | -9.3192
| TRYWERYN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 2.2755 | 2.3485 | 2.3403 | 2.2266 | 2.1372 | 2.0122 | 1.908 | 1.7907 | 1.656 | 1.5377 | 1.4852 | 1.3078 | 1.1709 | 1.1179 | 1.2029
| TWYFORDS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 4.4388 | 4.609 | 4.5818 | 4.4122 | 4.2412 | 4.0202 | 3.7974 | 3.5595 | 3.3042 | 3.0416 | 2.8127 | 1.9326 | 0.73628 | -0.1725 | -0.11072
| TYWYN T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 3.2041 | 3.2283 | 3.0602 | 2.4816 | 2.0461 | 1.4087 | 0.79713 | 0.12453 | -0.68861 | -1.3862 | -1.8991 | -3.6193 | -5.2139 | -6.2736 | -6.4425
| WAENFAWR T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | 4.3571 | 4.4174 | 4.3323 | 3.9834 | 3.5794 | 3.1025 | 2.6234 | 2.0663 | 1.4691 | 0.91796 | 0.44953 | -1.0857 | -2.7595 | -2.9988 | -3.0767
| WELSHPOOL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 3.5204 | 3.6294 | 3.5923 | 3.3747 | 3.141 | 2.8917 | 2.6151 | 2.3418 | 2.0627 | 1.7654 | 1.4971 | 0.5657 | -0.71365 | -1.1479 | -0.96057
| WEM EAST T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 4.5612 | 4.6615 | 4.6392 | 4.4532 | 4.2647 | 4.0315 | 3.8063 | 3.577 | 2.9757 | 2.6962 | 2.1748 | 0.5326 | -1.1639 | -0.59175 | -0.12939
| WEM T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 2.6939 | 2.8243 | 2.7372 | 2.4219 | 2.0184 | 1.5808 | 1.1144 | 0.56754 | -0.034279 | -0.63019 | -1.181 | -2.8928 | -5.0001 | -5.4971 | -5.1298
| WERVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 4.2857 | 4.291 | 4.1869 | 3.8851 | 3.5006 | 3.0854 | 2.6472 | 2.1648 | 1.5909 | 1.0412 | 0.55089 | -0.85192 | -2.888 | -3.4176 | -3.3419
| WEST FELTON T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 1.0204 | 1.1047 | 1.0862 | 0.93296 | 0.76476 | 0.58177 | 0.38649 | 0.18934 | -0.01921 | -0.23212 | -0.43252 | -1.113 | -2.0311 | -2.2888 | -2.081
| WESTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.8673 | 3.1208 | 3.0254 | 2.5854 | 2.1076 | 1.5454 | 0.94636 | 0.29662 | -0.39211 | -1.0727 | -1.6846 | -3.9496 | -7.0321 | -8.9715 | -8.8137
| WHEELOCK T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 2.4286 | 2.644 | 2.5833 | 2.2223 | 1.8111 | 1.3282 | 0.80764 | 0.22598 | -0.40855 | -1.0254 | -1.5659 | -3.532 | -5.9487 | -7.3314 | -7.4103
| WHITCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 5.8571 | 6.1064 | 6.0872 | 5.808 | 5.504 | 5.1406 | 4.7417 | 4.3237 | 3.8841 | 3.4504 | 3.0718 | 1.6602 | -0.24605 | -1.2696 | -1.2598
| WIMPEYS PANT QUARRY T1 / WIMPEYS PANT QUARRY T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 1.0673 | 6.093 | 6.0655 | 5.8716 | 5.6339 | 5.3735 | 5.0831 | 4.7655 | 4.4365 | 4.0987 | 3.8075 | 2.7572 | 1.2854 | 0.77375 | 0.76172
| WINCHAM T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 5.1327 | 5.1718 | 5.1429 | 5.0157 | 4.881 | 4.7287 | 4.5774 | 4.4176 | 4.266 | 4.0904 | 3.9306 | 3.3222 | 2.5079 | 2.2887 | 2.4341
| WISTASTON HALL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 3.0306 | 3.346 | 3.3613 | 3.1633 | 2.975 | 2.7521 | 2.4949 | 2.2146 | 1.9257 | 1.6136 | 1.317 | 0.32218 | -1.2558 | -2.2261 | -2.5857
| WRENBURY FRITH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 0.71429 | 0.8458 | 0.82259 | 0.67155 | 0.50783 | 0.31478 | 0.1182 | -0.084117 | -0.29099 | -0.505 | -0.68518 | -1.9787 | -4.0452 | -3.862 | -3.5801
| YOCKINGS GATE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | 6.5102 | 6.5284 | 6.4232 | 6.1553 | 5.8193 | 5.4516 | 5.0588 | 4.6113 | 4.1168 | 3.6085 | 3.1297 | 1.5572 | -0.36311 | -0.60454 | -0.22352
| YSBYTY GLAN CLWYD T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 3.602 | 3.7137 | 3.6943 | 3.4903 | 3.313 | 3.0955 | 2.8844 | 2.6829 | 2.4851 | 2.2665 | 2.0702 | 1.2459 | 0.23216 | 0.14023 | 0.31583
Grid Groups | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 33 | SWANSEA NORTH | 5.4006 | 7.5567 | 7.5977 | 2.0761 | 1.3827 | 5.8457 | -0.17464 | -4.9842 | -10.3993 | -15.4384 | -19.4703 | -33.0927 | -48.6687 | -53.0562 | -50.7883
| HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 18.2377 | 26.4048 | 25.2561 | 19.0592 | 12.2608 | 4.0107 | -4.5772 | -14.0507 | -24.9388 | -35.2163 | -43.9998 | -73.5063 | -106.5262 | -115.1024 | -110.328
| FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 33 | TRAWSFYNYDD | 5.1027 | 5.7817 | 3.9274 | 1.8296 | 9.1959 | 0.093215 | -9.0074 | -19.1087 | -30.8624 | -41.4269 | -49.9086 | -75.3059 | -101.3871 | -104.909 | -102.3826
| COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 33 | CELLARHEAD | 47.6799 | 52.9695 | 29.6183 | 14.7721 | 21.8784 | 4.074 | -6.1155 | -26.789 | -38.787 | -50.6102 | -61.6962 | -104.4975 | -162.2735 | -188.9214 | -187.7418
| GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 33 | KIRKBY | 39.9913 | 42.2717 | 42.3208 | 40.5651 | 39.0609 | 37.043 | 35.0996 | 33.2379 | 31.5476 | 29.5748 | 27.8711 | 19.4121 | 7.7441 | 1.2451 | 3.8001
| GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 33 | LISTER DRIVE | 53.4605 | 55.8876 | 55.9318 | 53.763 | 51.7775 | 49.4137 | 47.1044 | 44.468 | 42.084 | 39.306 | 36.6272 | 26.3897 | 10.3135 | 4.7011 | 5.3332
| FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 33 | KIRKBY | 7.639 | 11.0107 | 10.6505 | 34.7657 | 31.7745 | 27.056 | 20.2708 | 14.677 | 8.9321 | 3.1499 | -1.8959 | -20.8579 | -44.5202 | -55.3873 | -54.9167
| AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 33 | KIRKBY | 13.674 | 16.0398 | 16.0152 | 13.747 | 11.7879 | 9.3638 | 6.8838 | 4.3437 | 1.959 | -0.71361 | -3.179 | -13.1269 | -27.7539 | -34.0084 | -35.1953
| CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 44.2891 | 47.6743 | 47.3548 | 43.1423 | 38.8282 | 33.6166 | 28.3752 | 22.876 | 17.3523 | 11.5227 | 6.4211 | -12.6303 | -37.299 | -47.7512 | -44.3371
| LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 33 | LISTER DRIVE | 47.1083 | 52.5422 | 52.6722 | 50.6487 | 49.0855 | 45.8192 | 43.7583 | 41.8167 | 40.202 | 38.0602 | 36.2027 | 27.1385 | 13.1013 | 11.1299 | 15.5401
| BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 33 | RAINHILL | 42.7313 | 43.4336 | 43.2179 | 42.0915 | 40.9056 | 39.4022 | 37.8515 | 36.1413 | 34.3271 | 32.4338 | 30.7129 | 24.0421 | 14.7499 | 9.2196 | 8.4704
| AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 33 | KIRKBY | 24.4042 | 28.1855 | 27.2267 | 22.1829 | 16.2966 | 10.7889 | 1.3189 | -7.3591 | -16.7136 | -26.2381 | -34.5827 | -65.167 | -102.134 | -116.2988 | -114.2435
| AMLWCH GT1 / CAERGEILIOG GT1 | 33 | WYLFA | 18.4952 | 19.0035 | 17.6718 | 13.0867 | 7.8299 | 1.7679 | -4.4527 | -11.5744 | -19.5821 | -27.2462 | -33.9492 | -55.2341 | -80.9128 | -87.1865 | -85.0752
| HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | 34.3705 | 37.1874 | 36.5923 | 31.7091 | 26.9175 | 21.0845 | 15.1668 | 8.9522 | 2.4454 | -4.1643 | -9.7973 | -30.7805 | -58.7094 | -68.4221 | -67.6885
| BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 33 | RAINHILL | 22.297 | 19.944 | 13.2472 | 9.3627 | 5.6381 | 0.85694 | -3.9395 | -8.8113 | -13.5896 | -18.8386 | -23.4127 | -43.1327 | -69.1534 | -85.1437 | -80.3194
| HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 33 | BIRKENHEAD | 22.8417 | 24.825 | 23.912 | 18.9803 | 13.8199 | 7.5579 | 1.1891 | -5.6765 | -13.0786 | -20.3516 | -26.4763 | -48.0473 | -73.5447 | -83.7282 | -82.9227
| BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 33 | LEGACY | 28.3187 | 31.8011 | 30.3318 | 23.2713 | 17.2039 | 9.6642 | 2.0677 | -9.1252 | -17.1083 | -25.1738 | -32.5899 | -62.7903 | -101.9838 | -117.366 | -138.01
| CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 33 | CAPENHURST | 32.8049 | 36.704 | 35.9218 | 20.5368 | 15.2388 | 8.5324 | 1.5954 | -5.9368 | -13.934 | -21.9944 | -28.9586 | -55.2645 | -88.0972 | -103.145 | -100.4918
| DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 33 | FRODSHAM - INCE | 32.0789 | 35.6577 | 35.1625 | 32.1697 | 30.393 | 27.9344 | 25.2908 | 20.41 | 17.7898 | 15.0604 | -0.62465 | -13.2951 | -31.7772 | -41.6096 | -41.1814
| BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 33 | LISTER DRIVE | 68.4328 | 71.3976 | 71.1691 | 68.69 | 67.0841 | 65.0055 | 62.9915 | 52.823 | 50.7727 | 48.6066 | 46.0292 | 35.354 | 18.3351 | 14.9336 | 19.3305
| BANGOR GT2 / CAERNARFON GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 17.3986 | 20.1065 | 19.6347 | 15.7083 | 11.5778 | 6.7192 | 1.9485 | -3.5709 | -9.4187 | -15.3293 | -20.3667 | -38.3502 | -60.2611 | -66.0629 | -60.14
| DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 33 | CARRINGTON - FIDDLERS FERRY | 16.0845 | 19.0076 | 17.9089 | 13.0267 | 18.7441 | 14.8407 | -2.9749 | -33.6759 | -40.3608 | -47.1835 | -53.4402 | -79.1166 | -112.8329 | -129.7649 | -127.7063
| OSWESTRY GT5 / WHITCHURCH GT1 | 33 | LEGACY | 12.3187 | 14.7014 | 14.2589 | 11.1297 | 7.6906 | 3.7105 | -0.41213 | -4.9906 | -10.2964 | -15.2824 | -20.0267 | -36.2543 | -56.4805 | -61.2811 | -57.4568
| GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 33 | RAINHILL | 28.9061 | 33.0153 | 32.6289 | 28.0006 | 23.1459 | 17.0007 | 10.66 | 3.7428 | -3.4192 | -10.9504 | -17.5704 | -43.3057 | -75.4196 | -86.6294 | -84.2127
| PRENTON GRID GT1 / ROCK FERRY GT1 | 33 | BIRKENHEAD | 20.1231 | 22.5882 | 22.1066 | 21.9194 | 20.9741 | 21.6144 | 7.9302 | 3.4578 | -1.2696 | -6.1183 | -10.4085 | -26.473 | -47.3998 | -58.7475 | -55.7182
| COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 24.674 | 27.7096 | 26.7371 | 21.6208 | 16.2186 | 9.6278 | 2.6449 | -4.8152 | -13.2379 | -21.1117 | -27.5318 | -48.4215 | -73.2711 | -80.4753 | -78.2215
| BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 33 | LISTER DRIVE | 35.3334 | 41.3131 | 42.0998 | 39.4572 | 37.4286 | 34.7698 | 32.2617 | 26.2548 | 24.619 | 22.2346 | 20.0995 | 8.9157 | -7.7962 | -10.7314 | -6.6992
| ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 33 | FRODSHAM - INCE | 29.0962 | 32.9167 | 32.4263 | 28.4025 | 24.7411 | 20.4446 | 16.2961 | 7.1894 | 3.0367 | -1.2438 | -5.1808 | -20.0892 | -38.6344 | -41.5516 | -35.6425
| BOOTLE GT1 / LITHERLAND GT1A | 33 | KIRKBY | 20.6186 | 22.7682 | 22.7222 | 20.4948 | 18.6108 | 16.3421 | 14.1186 | 11.884 | 9.9458 | 7.735 | 5.6822 | -3.1738 | -15.4505 | -19.3328 | -19.0074
| BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 33 | CAPENHURST | -0.21633 | 4.0622 | 17.3877 | 12.8548 | 8.7131 | 3.5799 | -1.4841 | -12.2083 | -17.0774 | -22.252 | -26.8926 | -46.3038 | -71.7088 | -82.7703 | -80.34
| LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 33 | LEGACY | 63.2856 | 66.2077 | 64.4257 | 58.3484 | 50.4924 | 52.5813 | 41.3608 | 29.5025 | 16.1894 | 3.5254 | -7.0959 | -43.2829 | -87.1177 | -100.1422 | -97.7421
| SANKEY BRIDGES GT3 / WARRINGTON GT5 | 33 | CARRINGTON - FIDDLERS FERRY | 6.4157 | 10.058 | 10.1084 | 7.1745 | 4.3694 | 0.90953 | -2.5992 | -6.1468 | -9.5674 | -13.3854 | -16.7481 | -30.0133 | -48.3215 | -54.8195 | -52.8006
| RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 33 | RAINHILL | 25.6959 | 27.7513 | 27.6657 | 25.5419 | 23.4935 | 21.0489 | 18.6278 | 12.6594 | 10.2826 | 7.7 | 5.425 | -3.8892 | -16.7284 | -22.9904 | -21.621
| BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 18.7888 | 26.3446 | 30.8758 | 18.5747 | 17.1491 | 13.5243 | -3.5372 | -7.8349 | -12.1946 | -16.7354 | -20.6166 | -35.5362 | -54.8343 | -62.0573 | -60.5322
| BROMBOROUGH GT3 / ROCK FERRY GT2 | 33 | BIRKENHEAD | 23.5724 | 24.8835 | 24.3692 | 21.3718 | 18.5622 | 15.1354 | 11.7311 | -1.5853 | -5.128 | -8.8522 | -12.1985 | -25.4906 | -41.8506 | -48.529 | -46.3289
| WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 33 | BIRKENHEAD | 34.461 | 38.5572 | 38.8793 | 36.7408 | 34.9112 | 32.5198 | 30.0991 | 27.6054 | 25.1839 | 22.6299 | 20.6054 | 12.3558 | 1.6355 | -1.7883 | -1.7344
| ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | 27.1667 | 28.8637 | 28.2887 | 24.6784 | 20.8295 | 16.354 | 11.8852 | 5.9408 | 1.0184 | -4.0377 | -8.5785 | -25.1161 | -46.9356 | -53.7265 | -52.5877
| HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 33 | RAINHILL | 36.5594 | 36.0295 | 35.8971 | 34.5227 | 33.1724 | 31.4848 | 29.7644 | 27.9929 | 26.2386 | 24.3629 | 22.714 | 15.7439 | 6.4769 | 0.39564 | 1.8448
| DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | 12.7574 | 1.7281 | 1.7375 | 0.3389 | -0.80149 | 127.8527 | 126.674 | 125.7035 | 124.9904 | 123.943 | 122.9154 | 117.573 | 109.4602 | 107.9633 | 110.2754

## Baseline Scenario (Gen)
Generation Headroom (MW)
Return to Contents |  |  |  | Subject to upstream constraints beyond our network boundary (Yes/No) (See section 7.3 of the methodology statement) | Expected upsteam capacity release date (provided by National Grid Electricity Transmission) | Synchronous | [14 empty] | Fully Converted
| Group Name | Voltage (kV) | Grid / GSP Group |  |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050
Primary Groups | ABERDYFI T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 7.0173 | 6.9919 | 7.0005 | 6.9904 | 6.9769 | 6.983 | 6.9735 | 6.9851 | 7.0136 | 7.0323 | 7.0034 | 6.9399 | 6.7084 | 6.4009 | 5.9542 | 7.0173 | 6.9919 | 7.0005 | 6.9904 | 6.9769 | 6.983 | 6.9735 | 6.9851 | 7.0136 | 7.0323 | 7.0034 | 6.9399 | 6.7084 | 6.4009 | 5.9542
| ABERGELE T1 / PENSARN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 1.6617 | 1.607 | 1.5843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6617 | 1.607 | 1.5843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ABERSOCH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023432 | 0 | 0 | 0 | 0 | 0
| ABERYSTWYTH T1 / NORTH RD T1 / PARC-Y-LLYN T1 / PARC-Y-LLYN T2 / U C WALES T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 5.1952 | 5.1941 | 5.1865 | 5.1553 | 5.1187 | 5.0776 | 5.0334 | 4.9888 | 4.943 | 4.8921 | 4.8398 | 4.6809 | 4.3933 | 4.0858 | 3.7678 | 5.4223 | 5.2506 | 5.2473 | 5.3689 | 5.4691 | 5.6185 | 5.752 | 5.9083 | 6.0687 | 6.2067 | 6.2609 | 6.7205 | 7.0118 | 6.1739 | 4.3725
| ACER AVE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACORNFIELD RD T1 / DICKINSONS T1 / HAMMOND RD T1 / KODAK T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIGBURTH VALE T1 / IVY AVE T1 / MATHER AVE T1 / MOSSLEY HILL T1 / WAVERTREE T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AINSDALE T1 / PINFOLD LA T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 0.49443 | 0.43196 | 0.45205 | 0.37485 | 0.25616 | 0.15543 | 0.069925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49443 | 0.43196 | 0.45205 | 0.37485 | 0.25616 | 0.15543 | 0.069925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AINTREE LOCAL T1 / OLD ROAN T1 / WANGO LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 2.3344 | 2.2388 | 2.2385 | 2.195 | 2.0951 | 2.0149 | 1.9247 | 1.8454 | 1.7456 | 0.59501 | 0 | 0 | 0 | 0 | 0 | 2.3344 | 2.2388 | 2.2385 | 2.195 | 2.0951 | 2.0149 | 1.9247 | 1.8454 | 1.7456 | 0.59501 | 0 | 0 | 0 | 0 | 0
| AIRBUS T1 / BROUGHTON RETAIL PARK T1 / MIXALLOY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 1.3332 | 0.43308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3332 | 0.43308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIRPORT T1 / ALDERWOOD AVE (CROYDE RD) T1 / HAREFIELD RD T1 / METAL BOX (SPEKE) T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALBERT DOCK T1 / KINGS DOCK T1 / KINGS DOCK T2 / WAPPING T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALLERTON T1 / ECP WEST-BANKS RD T1 / GARSTON T1 / WEAVER IND EST T1 / YEW TREE RD T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALMATEX T1 / ST HELENS WWTW T1 / WATERY LA T2 / ex DELTA METALS T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0.24685 | 0.24685 | 0.24685 | 0.23629 | 0.20327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2343 | 1.2343 | 1.2343 | 1.1814 | 1.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALMONDS TURN T1 / ATLANTIC COMPLEX T1 / GIRO T1 / MIDLAND BANK T1 / NETHERTON T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 1.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALPOCO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0079882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0079882 | 0 | 0 | 0 | 0 | 0
| AMLWCH T1 / AMLWCH T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ANDERTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| APPLETON T1 / HORNSBRIDGE T1 / LUGSDALE T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 2.6859 | 2.6929 | 2.5532 | 2.3815 | 0 | 2.1048 | 1.9564 | 1.8416 | 1.6756 | 1.4764 | 1.1603 | 0.095843 | 0 | 0 | 0 | 2.6859 | 2.6929 | 2.5532 | 2.3815 | 0 | 2.1048 | 1.9564 | 1.8416 | 1.6756 | 1.4764 | 1.1603 | 0.095843 | 0 | 0
| ARROWE PK HOSP T1 / CHAMPION PLUGS T1 / CHAMPION PLUGS T2 / WOODCHURCH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1253 | 0.4926 | 0.49064 | 0.19861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1253 | 0.4926 | 0.49064 | 0.19861
| ARUNDEL T1 / GROVE PK T1 / WAVERTREE VALE T1 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASH RD T1 / KELLOGGS (WREXHAM) T1 / KELLOGGS (WREXHAM) T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 1.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASSOCIATED LEAD T1 / GREAT BOUGHTON T1 / PIPERS ASH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASTMOOR IND EST T1 / MACKAMAX T1 / MERSEY RD T1 / PICOW FARM RD T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ATHOL ST T1 / CHISENHALE ST T1 / SANDHILLS LA T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AUDLEM T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BALA T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.2554 | 9.1088 | 9.1283 | 9.1733 | 9.229 | 9.3017 | 9.3578 | 9.4399 | 9.5533 | 9.6278 | 0 | 0 | 0 | 0 | 0 | 9.2554 | 9.1088 | 9.1283 | 9.1733 | 9.229 | 9.3017 | 9.3578 | 9.4399 | 9.5533 | 9.6278 | 0 | 0 | 0 | 0 | 0
| BANASTRE RD T1 / DOVER RD T1 / GRANTHAM CL T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 2.1094 | 1.9506 | 1.9144 | 1.7856 | 1.6209 | 1.4587 | 1.2949 | 1.1566 | 0.98398 | 0.81293 | 0.59909 | 0.089656 | 0 | 0 | 0 | 2.1094 | 1.9506 | 1.9144 | 1.7856 | 1.6209 | 1.4587 | 1.2949 | 1.1566 | 0.98398 | 0.81293 | 0.59909 | 0.089656 | 0 | 0 | 0
| BANGOR HOSP T1 / BANGOR UNIVERSITY T1 / EITHINOG T1 / HIRAEL T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BARBAULD ST T1 / HORROCKS LA T1 / WARRINGTON CENTRAL T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.6497 | 1.616 | 1.6367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6497 | 1.616 | 1.6367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BARMOUTH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.8134 | 9.4326 | 9.4691 | 9.5458 | 9.602 | 9.681 | 9.7286 | 9.7897 | 9.8808 | 9.9419 | 0 | 0 | 0 | 0 | 0 | 9.8134 | 9.4326 | 9.4691 | 9.5458 | 9.602 | 9.681 | 9.7286 | 9.7897 | 9.8808 | 9.9419 | 0 | 0 | 0 | 0 | 0
| BARNSTON T1 / GAYTON T1 / IRBY T1 / THINGWALL T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 4.6697 | 4.508 | 4.3874 | 4.3337 | 4.2227 | 4.1195 | 4.0036 | 3.9112 | 3.8526 | 3.6732 | 3.4029 | 2.6434 | 0.079196 | 0 | 0 | 4.6697 | 4.508 | 4.3874 | 4.3337 | 4.2227 | 4.1195 | 4.0036 | 3.9112 | 3.8526 | 3.6732 | 3.4029 | 2.6434 | 0.079196 | 0 | 0
| BASCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BASS CHARRINGTON T1 / BASS CHARRINGTON T2 / CLIFTON T1 / YKK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 2.5478 | 2.3923 | 2.3575 | 2.3852 | 2.3726 | 2.3837 | 2.3682 | 2.3507 | 2.2772 | 2.2459 | 2.1903 | 2.2217 | 2.107 | 1.4068 | 0.065682 | 2.5478 | 2.3923 | 2.3575 | 2.3852 | 2.3726 | 2.3837 | 2.3682 | 2.3507 | 2.2772 | 2.2459 | 2.1903 | 2.2217 | 2.107 | 1.4068 | 0.065682
| BATTERSBY LA T1 / RYLANDS ELDON ST T2 | 6 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEAUMARIS T1 / BEAUMARIS T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.2973 | 10.303 | 10.3388 | 10.3785 | 10.4298 | 10.4871 | 10.5569 | 10.637 | 10.7372 | 9.6569 | 0 | 0 | 0 | 0 | 0 | 10.2973 | 10.303 | 10.3388 | 10.3785 | 10.4298 | 10.4871 | 10.5569 | 10.637 | 10.7372 | 9.6569 | 0 | 0 | 0 | 0 | 0
| BEAUMONT ST T1 / DINGLE VALE T1 / LARK LA T1 / MDHB BRUNSWICK DOCK T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEDBURN DV T1 / BLUEBELL LA T1 / BROOKBRIDGE T1 / ECCLESTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEECH ST T1 / LISTER DV A T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEMROSE T1 / CARR LA EAST T1 / LUCAS (FAZAKERLEY) T1 / NORRIS GREEN T1 / WEST DERBY T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 3.6551 | 3.6504 | 3.6255 | 3.5418 | 3.4488 | 3.3429 | 3.2314 | 3.1156 | 2.9954 | 0.59501 | 0 | 0 | 0 | 0 | 0 | 5.2394 | 4.9826 | 4.8718 | 4.7046 | 4.4589 | 4.1971 | 3.9208 | 3.6263 | 3.3041 | 0.59501 | 0 | 0 | 0 | 0 | 0
| BENTINCK ST T1 / BENTINCK ST T2 / CHESTER ST T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BERSHAM COLLIERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 4.4247 | 4.4041 | 4.406 | 4.3814 | 4.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4247 | 4.4041 | 4.406 | 4.3814 | 4.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BERSHAM RD T1 / IND COOPE T1 / RHYD BROUGHTON LA T1 / TUTTLE ST T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 3.4097 | 3.2522 | 3.2473 | 3.3016 | 3.3145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4097 | 3.2522 | 3.2473 | 3.3016 | 3.3145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BETHESDA T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BETWS-Y-COED T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 9.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEWSEY T1 / OWEN ST T1 / RODNEY ST T1 / RYLANDS ELDON ST T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 3.7892 | 3.6566 | 3.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7892 | 3.6566 | 3.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BIBBYS T1 / INLAND REVENUE OFFICES T1 / REGENT RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BICC HUYTON QUARRY T1 / TARBOCK T1 / WHISTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BICC WREXHAM T1 / MARCHWIEL T1 / WIE CENTRAL T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 2.7472 | 2.398 | 2.2846 | 2.2751 | 2.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7472 | 2.398 | 2.2846 | 2.2751 | 2.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BIRKENHEAD CENTRAL T1 / SINGLETON AVE T1 / TRANMERE T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ex BIXTETH ST T1 / LITTLEWOODS T1 / PALL MALL T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLACON T1 / COCOA BARRY T1 / CRANE BANK T1 / KNUTSFORD WAY T1 / TOWER WHARF T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLAENAU FFESTINIOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLUNDELL ST T1 / ROPEWALKS T1 / ST JAMES T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLUNDELLSANDS (NORTH) T1 / BLUNDELLSANDS (SOUTH) T1 / CROSBY T1 / KERSHAW AVE T1 / WATERLOO T2 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 3.6144 | 3.6082 | 3.5745 | 3.4759 | 3.3618 | 3.2352 | 3.0985 | 2.9598 | 2.8114 | 2.6503 | 2.487 | 1.9745 | 1.0536 | 0 | 0 | 5.6869 | 5.4447 | 5.3745 | 5.2755 | 5.1778 | 5.1246 | 5.054 | 5.048 | 5.0626 | 5.0338 | 4.9058 | 4.8041 | 3.1172 | 0 | 0
| BODFARI PRODUCERS T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOLTON ST T1 / GREEK ST T1 / HPO COPPERAS HILL T1 / OLDHAM PLACE T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GRID T1 / KELLOGGS T1 / PACIFIC RD T1 / WASHINGTON ST T1 / WATERLOO T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GRID T2 / ORRELL MOUNT T1 / SCARISBRICK AVE T1 / TATTON RD T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4145 | 0 | 0
| BOTWNNOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOULEVARD T1 / CHAPELFORD T1 / HAWLEYS LA T1 / WESTBROOK T1 / WINWICK QUAY T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.9326 | 1.929 | 1.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9672 | 3.7662 | 3.7214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOW ST T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 6.4873 | 6.2999 | 6.2396 | 6.1837 | 6.135 | 6.1065 | 6.0949 | 6.0829 | 6.0797 | 6.0123 | 5.8172 | 5.0081 | 3.7671 | 0.44161 | 0 | 6.4873 | 6.2999 | 6.2396 | 6.1837 | 6.135 | 6.1065 | 6.0949 | 6.0829 | 6.0797 | 6.0123 | 5.8172 | 5.0081 | 3.7671 | 0.44161 | 0
| BOWATER CONTAINERS T1 / ELLESMERE PORT LOCAL T1 / HH ROBERTSONS T1 / MOBIL OIL (E PORT) T1 / WHITBY T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BR STATION T1 / DUCHY RD T1 / ELECTRA WAY T1 / MIDLAND ROLLMAKERS T1A / NORTH WESTERN MILLS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH ALUMINIUM LATCHFORD T1 / GREENHALL WHITLEY T1 / LATCHFORD T1 / LATCHFORD T2 / THAMES BOARD MILL T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 1.7948 | 1.6584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9397 | 2.9039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH OXYGEN T1 / WINDLEHURST T1 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0.36383 | 0.27834 | 0.28071 | 0.21862 | 0.098556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36383 | 0.27834 | 0.28071 | 0.21862 | 0.098556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH PIPE ASSOCIATION T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH SIDAC T1 / SHERDLEY RD T1 / ST HELENS LINKWAY T1 / WATERY LA T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROADGREEN T1 / CROXTETH T1 / EAST PRESCOT RD (FINCH LA) T1 / KNOTTY ASH T1 / LEYFIELD RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMFIELD T1 / BROMFIELD T2 / PONTERWYL T1 / RHYD-Y-GOLEU T1 / SYNTHITE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 3.262 | 3.2573 | 3.2345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3332 | 4.161 | 4.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROOK LA T1 / MANNINGS LA T1 / NEWTOWN CHESTER T1 / UPTON HEATH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROOK ST T1 / KINGSWAY TUNNEL T1 / NWWA SANDON DOCK T1 / NWWA SANDON DOCK T2 | 11 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRYN STANLEY T1 / DENBIGH T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUCKINGHAM ST T1 / EVERTON RD T1 / SUBURBAN RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUCKLEY T1 / BUCKLEY T2 / BUCKLEY CROSS T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0.87167 | 0.728 | 0.6425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87167 | 0.728 | 0.6425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUILDWAS RD T1 / MORGAN REFRACTORIES T1 / NESTON MAIN T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 1.9597 | 1.9175 | 1.909 | 1.8877 | 1.854 | 1.8395 | 1.8013 | 1.6287 | 1.313 | 1.1286 | 1.0462 | 0.89326 | 0 | 0 | 0 | 1.9597 | 1.9175 | 1.909 | 1.8877 | 1.854 | 1.8395 | 1.8013 | 1.6287 | 1.313 | 1.1286 | 1.0462 | 0.89326 | 0 | 0 | 0
| BURLINGTON AVE T1 / FRESHFIELD T1 / MARSH BROWS T1 / SOUTHPORT RD T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 1.7919 | 1.6235 | 1.5466 | 1.4114 | 1.2309 | 1.0522 | 0.88728 | 0.70374 | 0.50454 | 0.27183 | 0 | 0 | 0 | 0 | 0 | 1.7919 | 1.6235 | 1.5466 | 1.4114 | 1.2309 | 1.0522 | 0.88728 | 0.70374 | 0.50454 | 0.27183 | 0 | 0 | 0 | 0 | 0
| BURMAH OIL T1 / CABOT CARBON T1 / VAN LEER NO 1 T1 | 7 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.71032 | 0.67668 | 0.67393 | 0.69713 | 0.6843 | 0.68155 | 0.67481 | 0.66844 | 0.65233 | 0.64763 | 0.64624 | 0.72434 | 0.88488 | 0.9182 | 0.84546 | 0.71032 | 0.67668 | 0.67393 | 0.69713 | 0.6843 | 0.68155 | 0.67481 | 0.66844 | 0.65233 | 0.64763 | 0.64624 | 0.72434 | 0.88488 | 0.9182 | 0.84546
| BUTLINS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 3.3324 | 3.1103 | 3.0133 | 2.9449 | 2.7092 | 2.5038 | 1.9765 | 1.3532 | 0.77526 | 0.22805 | 0 | 0 | 0 | 0 | 0 | 3.3324 | 3.1103 | 3.0133 | 2.9449 | 2.7092 | 2.5038 | 1.9765 | 1.3532 | 0.77526 | 0.22805 | 0 | 0 | 0 | 0 | 0
| BUTTINGTON CROSS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.0422 | 7.0076 | 7.0106 | 7.014 | 6.9777 | 6.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0422 | 7.0076 | 7.0106 | 7.014 | 6.9777 | 6.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BXL BROMBOROUGH T1 / TULIP T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0.4497 | 0.41319 | 0.41514 | 0.4609 | 0.44787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4497 | 0.41319 | 0.41514 | 0.4609 | 0.44787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CABLE ST T1 / GRADWELL ST T2 / OLDHAM PLACE T2 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CABLE ST T2 / CROWN COURTS T1 / GRADWELL ST T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CADBURYS KRONOSPAN T1 / CADBURYS KRONOSPAN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.5922 | 0.54382 | 0.55485 | 0.56466 | 0.55091 | 0.55766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5922 | 0.54382 | 0.55485 | 0.56466 | 0.55091 | 0.55766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CADBURYS T1 / CADBURYS T2 / HOPFIELD RD T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAERGEILIOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.34479 | 0.33 | 0.33316 | 0.33401 | 0.37383 | 0.38572 | 0.39442 | 0.46022 | 0.54614 | 0.61741 | 0 | 0 | 0 | 0 | 0 | 0.34479 | 0.33 | 0.33316 | 0.33401 | 0.37383 | 0.38572 | 0.39442 | 0.46022 | 0.54614 | 0.61741 | 0 | 0 | 0 | 0 | 0
| CAERGWRLE T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0.62167 | 0.56887 | 0.54482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62167 | 0.56887 | 0.54482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAERNARFON T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0.029175 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040376 | 0.10559 | 0.20675 | 0.27243 | 0.58048 | 0.78347 | 0.24856 | 0 | 0.029175 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040376 | 0.10559 | 0.20675 | 0.27243 | 0.58048 | 0.78347 | 0.24856 | 0
| CAERSWS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9557 | 6.3208 | 6.3195 | 6.2702 | 6.185 | 6.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9557 | 6.3208 | 6.3195 | 6.2702 | 6.185 | 6.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CALDY T1 / HOYLAKE T1 / MEOLS T1 / WEST KIRBY SOUTH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 4.0572 | 3.9014 | 3.825 | 3.8178 | 3.742 | 3.6969 | 3.6439 | 3.5525 | 3.5301 | 3.4251 | 3.1742 | 2.5252 | 0.70798 | 0 | 0 | 4.0572 | 3.9014 | 3.825 | 3.8178 | 3.742 | 3.6969 | 3.6439 | 3.5525 | 3.5301 | 3.4251 | 3.1742 | 2.5252 | 0.70798 | 0 | 0
| CARBORUNDUM T1 / HOUGHTONS LA T1 / RAINFORD T1 / WINDLEHURST T2 | 11 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0.023834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CARLTON ST T1 / CARLTON ST T2 / CHALON WAY T2 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CARMEL T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.9274 | 2.318 | 2.2753 | 2.2159 | 2.1773 | 2.0603 | 1.7265 | 1.3812 | 1.0493 | 0.6248 | 0 | 0 | 0 | 0 | 0 | 2.9274 | 2.318 | 2.2753 | 2.2159 | 2.1773 | 2.0603 | 1.7265 | 1.3812 | 1.0493 | 0.6248 | 0 | 0 | 0 | 0 | 0
| CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 11 | CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | Yes | 2037 | 3.0747 | 2.0293 | 2.1735 | 2.1581 | 2.0903 | 2.0268 | 1.9235 | 1.8432 | 1.744 | 1.6365 | 1.5289 | 1.1761 | 0 | 0 | 0 | 4.5072 | 3.3695 | 3.4194 | 3.4001 | 3.25 | 3.1422 | 2.9802 | 2.8218 | 2.6523 | 2.4508 | 2.181 | 1.4547 | 0 | 0 | 0
| CEFN MAWR T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0.044175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CEMAES BAY T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 3.2823 | 3.2852 | 3.3061 | 3.3102 | 3.3223 | 3.3361 | 3.3595 | 3.3888 | 3.4365 | 3.4563 | 0 | 0 | 0 | 0 | 0 | 3.2823 | 3.2852 | 3.3061 | 3.3102 | 3.3223 | 3.3361 | 3.3595 | 3.3888 | 3.4365 | 3.4563 | 0 | 0 | 0 | 0 | 0
| CEMMAES RD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.8189 | 2.6221 | 2.5669 | 2.5357 | 2.4951 | 2.4862 | 2.4936 | 2.4742 | 2.4877 | 2.4261 | 0 | 0 | 0 | 0 | 0 | 2.8189 | 2.6221 | 2.5669 | 2.5357 | 2.4951 | 2.4862 | 2.4936 | 2.4742 | 2.4877 | 2.4261 | 0 | 0 | 0 | 0 | 0
| CEREAL PARTNERS T1 / LEVER GEORGIA AVE T1 / POOL LA T1 / UML LEVER BROMBOROUGH T2 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHALON WAY T1 / TECHNOLOGY CAMPUS T1 / WOODVILLE ST T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 1.1613 | 1.0959 | 1.1006 | 1.0533 | 0.92279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1613 | 1.0959 | 1.1006 | 1.0533 | 0.92279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESHIRE GREEN T1 / NWF T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESTER GATES T1 / UNILEVER DUNKIRK T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESTER ST (WREXHAM) T1 / EAGLES MEADOW T1 / RHOSNESNI T1 / WHITEGATE T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 3.4147 | 3.26 | 3.2547 | 3.2574 | 3.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4147 | 3.26 | 3.2547 | 3.2574 | 3.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHILDWALL T1 / CHILDWALL FIVEWAYS T1 / LYNDENE RD T1 / MIDDLEMASS HEY T1 / NAYLORS RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHOWLEY T1 / CHOWLEY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 10.1997 | 10.1292 | 10.1323 | 10.0902 | 10.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1997 | 10.1292 | 10.1323 | 10.0902 | 10.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHURCH LA T1 / NANT HALL T1 / PRESTATYN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 2.4967 | 2.3927 | 2.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 2.3927 | 2.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHURCH LAWTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHURCH ST WINSFORD T1 / OVER T1 / WHARTON PK T1 / WOODFORD PK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 4.2572 | 4.0447 | 3.992 | 3.9325 | 3.843 | 3.7882 | 3.7346 | 3.6772 | 3.6277 | 3.5179 | 3.3558 | 3.0684 | 1.8641 | 0 | 0 | 4.2572 | 4.0447 | 3.992 | 3.9325 | 3.843 | 3.7882 | 3.7346 | 3.6772 | 3.6277 | 3.5179 | 3.3558 | 3.0684 | 1.8641 | 0 | 0
| CIVIC CENTRE T1 / CLAUGHTON AVE T1 / ELECTRICITY ST T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLEDFORD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLOCKFACE T1 / GEC ST HELENS T1 / HILLS MOSS T1 / NCB SUTTON MANOR T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLUBMOOR T1 / DUNLOPS WALTON T1 / WALTON T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLUBMOOR T2 / LISTER DV A T1 / SUBURBAN RD T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COEDPOETH T1 / COEDPOETH T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.3947 | 7.358 | 7.3891 | 7.4343 | 7.4786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3947 | 7.358 | 7.3891 | 7.4343 | 7.4786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COLWYN BAY T1 / COLWYN BAY T2 / RHOS-ON-SEA T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 1.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONEY GREEN T1 / OSWESTRY T2 / OSWESTRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 2.3897 | 2.067 | 1.8039 | 1.2023 | 0.75785 | 0.36572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3897 | 2.067 | 1.8039 | 1.2023 | 0.75785 | 0.36572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONIX T1 / CONIX T2 / MEDEVA T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONNAHS QUAY LOCAL T1 / CONNAHS QUAY LOCAL T2 / HAWARDEN T1 / KING GEORGE ST T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 3.3392 | 2.9612 | 2.6991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3392 | 2.9612 | 2.6991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONWY T1 / DEGANWY T1 / LLANDUDNO JUNCTION T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CORWEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 7.0154 | 6.6289 | 6.6092 | 6.61 | 6.5796 | 6.4798 | 6.4639 | 6.3846 | 6.3321 | 6.1766 | 0 | 0 | 0 | 0 | 0 | 7.0154 | 6.6289 | 6.6092 | 6.61 | 6.5796 | 6.4798 | 6.4639 | 6.3846 | 6.3321 | 6.1766 | 0 | 0 | 0 | 0 | 0
| CREWE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRIGGION RADIO STATION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 2.9797 | 2.6289 | 2.609 | 2.5712 | 2.4858 | 2.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9797 | 2.6289 | 2.609 | 2.5712 | 2.4858 | 2.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CROSSFIELDS T1 / CROSSFIELDS T2 / LEVERS CROSSFIELDS T3 / GATEWARTH SEWAGE T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 0.94469 | 0.83583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94469 | 0.83583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CROWTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.22532 | 0.038589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22532 | 0.038589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CWM DYLI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.0724 | 1.8711 | 1.7731 | 1.6959 | 1.6233 | 1.5428 | 1.5086 | 1.4785 | 1.457 | 1.3821 | 0 | 0 | 0 | 0 | 0 | 2.0724 | 1.8711 | 1.7731 | 1.6959 | 1.6233 | 1.5428 | 1.5086 | 1.4785 | 1.457 | 1.3821 | 0 | 0 | 0 | 0 | 0
| DAILY POST & ECHO T1 / DAILY POST & ECHO T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DARESBURY NPL T1 / DARESBURY NPL T2 / DARESBURY PK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0.59032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DAVY WAY T1 / LLAY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE ALUMINIUM T1 / DUNLOP PLASTICS T1 / FIRESTONE T1 / TETRAPAK T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.9882 | 7.9253 | 7.9078 | 7.9823 | 7.9794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.14 | 7.9253 | 7.9078 | 8.1043 | 8.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE IND PK T1 / DEESIDE IND PK 6TH AVE T1 / RAF SEALAND T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | Yes | 2037 | 2.4077 | 2.3253 | 2.3413 | 2.432 | 2.5183 | 2.6196 | 2.7031 | 2.7983 | 2.8737 | 2.9691 | 3.077 | 3.5565 | 4.1545 | 4.0015 | 3.5487 | 2.4077 | 2.3253 | 2.3413 | 2.432 | 2.5183 | 2.6196 | 2.7031 | 2.7983 | 2.8737 | 2.9691 | 3.077 | 3.5565 | 4.1545 | 4.0015 | 3.5487
| DELAMORE ST T1 / KIRKDALE T1 / WALTON T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DESOTO RD T1 / MERSEY BRIDGE T1 / PITT ST T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 0.6152 | 0.60904 | 0.61072 | 0.50521 | 0 | 0.33263 | 0.26905 | 0.20743 | 0.1385 | 0.10176 | 0.072135 | 0.11802 | 0.013706 | 0 | 0 | 0.6152 | 0.60904 | 0.61072 | 0.50521 | 0 | 0.33263 | 0.26905 | 0.20743 | 0.1385 | 0.10176 | 0.072135 | 0.11802 | 0.013706 | 0
| DIBBINSDALE T1 / PLYMYARD T1 / WIBP HARDKNOTT RD T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 2.4447 | 2.3769 | 2.3685 | 2.3442 | 2.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4447 | 2.3769 | 2.3685 | 2.3442 | 2.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DINGLE T1 / GRANBY T1 / ST JAMES T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DITTON T1 / GAVIN RD T1 / HOUGH GREEN T1 / RTZ T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 3.9312 | 3.9422 | 3.82 | 3.6545 | 0 | 3.3929 | 3.2584 | 3.1177 | 2.9637 | 2.7465 | 2.4578 | 1.4495 | 0 | 0 | 0 | 3.9312 | 3.9422 | 3.82 | 3.6545 | 0 | 3.3929 | 3.2584 | 3.1177 | 2.9637 | 2.7465 | 2.4578 | 1.4495 | 0 | 0
| DODDS LA T1 / HOLBORN HILL T1 / MAGHULL T1 / MAGHULL T2 / ROBBINS BRIDGE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 3.5594 | 3.5504 | 3.4957 | 3.3693 | 3.2216 | 3.0521 | 2.8736 | 2.6852 | 2.4884 | 2.2736 | 2.0527 | 1.357 | 0 | 0 | 0 | 6.2994 | 5.8051 | 5.5755 | 5.2949 | 4.9816 | 4.6625 | 4.3516 | 4.0719 | 3.8008 | 3.4344 | 2.9369 | 1.5973 | 0 | 0 | 0
| DOLGARROG T1 / DOLGARROG T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DOLGELLAU T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 8.9984 | 8.9815 | 8.9965 | 9.0625 | 9.1114 | 9.1866 | 9.2532 | 9.3454 | 9.4775 | 9.5604 | 0 | 0 | 0 | 0 | 0 | 8.9984 | 8.9815 | 8.9965 | 9.0625 | 9.1114 | 9.1866 | 9.2532 | 9.3454 | 9.4775 | 9.5604 | 0 | 0 | 0 | 0 | 0
| DUCKINGTON T1 / DUCKINGTON T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DUDDON T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DYFFRYN ARDUDWY T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.8374 | 9.6672 | 9.613 | 9.6135 | 9.6045 | 9.6024 | 9.6166 | 9.5616 | 9.5671 | 9.4624 | 0 | 0 | 0 | 0 | 0 | 9.8374 | 9.6672 | 9.613 | 9.6135 | 9.6045 | 9.6024 | 9.6166 | 9.5616 | 9.5671 | 9.4624 | 0 | 0 | 0 | 0 | 0
| DYSERTH RD T1 / FFORDD LAS T1 / FFORDD LAS T2 / WESTBOURNE AVE T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 5.3492 | 4.9171 | 4.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3492 | 4.9171 | 4.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EDEN VALE T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 7.0847 | 7.0276 | 7.0273 | 6.9318 | 6.8186 | 6.7204 | 6.6156 | 6.5181 | 6.4272 | 6.3318 | 6.2144 | 6.0154 | 5.6986 | 0 | 0 | 7.0847 | 7.0276 | 7.0273 | 6.9318 | 6.8186 | 6.7204 | 6.6156 | 6.5181 | 6.4272 | 6.3318 | 6.2144 | 6.0154 | 5.6986 | 0 | 0
| EDERN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.07741 | 0.10036 | 0.12898 | 0.19096 | 0.24909 | 0.33013 | 0.4004 | 0.46832 | 0.58012 | 0.64511 | 0 | 0 | 0 | 0 | 0 | 0.07741 | 0.10036 | 0.12898 | 0.19096 | 0.24909 | 0.33013 | 0.4004 | 0.46832 | 0.58012 | 0.64511 | 0 | 0 | 0 | 0 | 0
| EDGE HILL T1 / LIVERPOOL UNIVERSITY T1 / LIVERPOOL UNIVERSITY T2 / LIVERPOOL UNIVERSITY T3 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EDGE LA (TAPLEY PLACE) T1 / LISTER DV B T3 / MILL LA (WAVERTREE) T1 / PLESSEY (EDGE LA) T1 / STONEYCROFT T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EGA ELECTRIC T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 6.4292 | 6.3739 | 6.3674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4292 | 6.3739 | 6.3674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EGERTON T1 / ROCK FERRY T1 / SHELL TRANMERE T1 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EGREMONT T1 / LISCARD T1 / POULTON T1 / STONE MANGANESE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELLESMERE T1 / MMB ELLESMERE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0 | 0 | 0.0060354 | 0.016803 | 0.011715 | 0.030259 | 0.040611 | 0.077314 | 0.10903 | 0.14956 | 0.17401 | 0.29881 | 0.28428 | 0 | 0 | 0 | 0 | 0.0060354 | 0.016803 | 0.011715 | 0.030259 | 0.040611 | 0.077314 | 0.10903 | 0.14956 | 0.17401 | 0.29881 | 0.28428 | 0 | 0
| ENGINEER PK T1 / PILKINGTONS QUEENSFERRY T1 / QUEENSFERRY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ESTUARY COMMERCE PK T1 / LEEWARD DR T1 / LEEWARD DR T2 / SPEKE HALL RD T1 / SPEKE SKY PK T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EVERTON BROW T1 / GARDNERS ROW T1 / SHEIL PK T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EXPRESS FOODS T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FAIRBOURNE T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 9.2548 | 9.0887 | 9.0604 | 9.0632 | 9.0321 | 9.0339 | 9.0512 | 8.9999 | 9.0482 | 8.9423 | 8.8402 | 8.6391 | 8.5012 | 6.1476 | 3.5054 | 9.2548 | 9.0887 | 9.0604 | 9.0632 | 9.0321 | 9.0339 | 9.0512 | 8.9999 | 9.0482 | 8.9423 | 8.8402 | 8.6391 | 8.5012 | 6.1476 | 3.5054
| FAZAKERLEY HOSPITAL T1 / JACOBS T1 / JACOBS T2 / SEEDS LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 3.3394 | 3.0907 | 3.058 | 3.0306 | 2.9442 | 2.8791 | 2.8415 | 2.787 | 2.741 | 0.59501 | 0 | 0 | 0 | 0 | 0 | 3.3394 | 3.0907 | 3.058 | 3.0306 | 2.9442 | 2.8791 | 2.8415 | 2.787 | 2.741 | 0.59501 | 0 | 0 | 0 | 0 | 0
| FERODO T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.6672 | 6.6519 | 6.6538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6672 | 6.6519 | 6.6538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FLINT T1 / FLINT T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FODENS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORD T1 / OXTON T1 / PRENTON LOCAL T1 / SINGLETON AVE T2 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORDEN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 3.4447 | 4.6099 | 4.5291 | 4.4169 | 4.281 | 4.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4447 | 4.6099 | 4.5291 | 4.4169 | 4.281 | 4.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FOUR CROSSES T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.5874 | 1.3128 | 0.8494 | 0.54002 | 0.37307 | 0.27493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5874 | 1.3128 | 0.8494 | 0.54002 | 0.37307 | 0.27493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRODSHAM LOCAL T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.79532 | 0.76199 | 0.78932 | 0.79236 | 0.76479 | 0.74215 | 0.72254 | 0.72627 | 0.73389 | 0.70958 | 0.65825 | 0.58135 | 0 | 0 | 0 | 0.79532 | 0.76199 | 0.78932 | 0.79236 | 0.76479 | 0.74215 | 0.72254 | 0.72627 | 0.73389 | 0.70958 | 0.65825 | 0.58135 | 0 | 0 | 0
| GADBROOK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 6.9272 | 6.8876 | 6.8949 | 6.8513 | 6.7671 | 6.6883 | 6.6195 | 6.5556 | 6.5144 | 6.463 | 6.4215 | 6.2938 | 6.0845 | 0 | 0 | 6.9272 | 6.8876 | 6.8949 | 6.8513 | 6.7671 | 6.6883 | 6.6195 | 6.5556 | 6.5144 | 6.463 | 6.4215 | 6.2938 | 6.0845 | 0 | 0
| GAERWEN VIEW T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 9.7898 | 9.7869 | 9.7925 | 9.7885 | 9.7809 | 9.7971 | 9.7873 | 9.7883 | 9.7925 | 9.6569 | 0 | 0 | 0 | 0 | 0 | 9.7898 | 9.7869 | 9.7925 | 9.7885 | 9.7809 | 9.7971 | 9.7873 | 9.7883 | 9.7925 | 9.6569 | 0 | 0 | 0 | 0 | 0
| GIGG LA THELWALL T1 / HILLCLIFFE T1 / STOCKTON HEATH T1 / STRETTON IND EST T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 4.8247 | 2.9039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8247 | 2.9039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GILBROOK DOCK T1 / HILL RD T1 / MOBIL OIL (WALLASEY) T1 | 7 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLAN-YR-AFON T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.35791 | 0.15506 | 0.062685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35791 | 0.15506 | 0.062685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GRAIG FAWR T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 8.0917 | 8.0996 | 8.1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0917 | 8.0996 | 8.1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GRAVEL T1 / WCB PLASTICS T1 / WHARTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 1.0897 | 1.0414 | 1.0457 | 1.0396 | 0.98147 | 0.95198 | 0.91546 | 0.8917 | 0.86274 | 0.85319 | 0.85772 | 0.91869 | 1.0201 | 0 | 0 | 1.0897 | 1.0414 | 1.0457 | 1.0396 | 0.98147 | 0.95198 | 0.91546 | 0.8917 | 0.86274 | 0.85319 | 0.85772 | 0.91869 | 1.0201 | 0 | 0
| GREASBY T1 / SAUGHALL MASSIE T1 / UPTON T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 2.7557 | 2.5992 | 2.5454 | 2.4914 | 2.3931 | 2.315 | 2.2074 | 2.1501 | 2.0642 | 1.9453 | 1.7797 | 1.4941 | 0.37162 | 0 | 0 | 2.7557 | 2.5992 | 2.5454 | 2.4914 | 2.3931 | 2.315 | 2.2074 | 2.1501 | 2.0642 | 1.9453 | 1.7797 | 1.4941 | 0.37162 | 0 | 0
| GREAT SANKEY T1 / PENKETH T1 / WIDNES RD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 2.1397 | 2.0538 | 2.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1397 | 2.0538 | 2.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GREAT SUTTON T1 / LITTLE SUTTON T1 / STRAWBERRY ROUNDABOUT T1 / SUTTON HALL WWB T1 / WHITBY MAIN T2 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GREENFIELD T1 / GREENFIELD T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GROSVENOR ST T1 / LINENHALL ST T1 / NORTHGATE TERRACE T1 / STATION VIEW T1 / TOMULAR PLACE T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GWERSYLLT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 9.8597 | 9.8441 | 9.8723 | 9.857 | 9.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8597 | 9.8441 | 9.8723 | 9.857 | 9.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HALTON RD T1 / MURDISHAW T1 / PERCIVAL LA T4 / RUNCORN CENTRAL T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARLECH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 6.8699 | 6.8003 | 6.8243 | 6.8573 | 6.8741 | 6.9181 | 6.9686 | 7.0148 | 7.0773 | 7.1161 | 0 | 0 | 0 | 0 | 0 | 6.8699 | 6.8003 | 6.8243 | 6.8573 | 6.8741 | 6.9181 | 6.9686 | 7.0148 | 7.0773 | 7.1161 | 0 | 0 | 0 | 0 | 0
| HARRINGTON ST T1 / PARADISE ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARRINGTON ST T2 / HIGHFIELD ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARRINGTON ST T3 / LIME ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARTFORD T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0.022192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HASKAYNE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HATHERTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HERONS WAY T1 / LACHE T1 / MBNA T1 / SMFS KINGSMEADOW T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HIGHFIELD ST T2 / LIME ST T2 / OLD HAYMARKET T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLMES CHAPEL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLT LA (WARRINGTON RD) T1 / PRESCOT T1 / RAINHILL LOCAL T1 / WHISTON HOSP T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 4.2929 | 4.2641 | 4.0585 | 3.8432 | 0 | 3.4993 | 3.3714 | 3.2317 | 3.0957 | 2.9147 | 2.6041 | 1.3671 | 0 | 0 | 0 | 4.2929 | 4.2641 | 4.0585 | 3.8432 | 0 | 3.4993 | 3.3714 | 3.2317 | 3.0957 | 2.9147 | 2.6041 | 1.3671 | 0 | 0
| HOLWAY RD T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 7.5997 | 7.572 | 5.9914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5997 | 7.572 | 5.9914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLYHEAD T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.024788 | 0.017331 | 0.036453 | 0.065138 | 0.099497 | 0.12893 | 0.17023 | 0.22631 | 0.28774 | 0.35463 | 0 | 0 | 0 | 0 | 0 | 0.024788 | 0.017331 | 0.036453 | 0.065138 | 0.099497 | 0.12893 | 0.17023 | 0.22631 | 0.28774 | 0.35463 | 0 | 0 | 0 | 0 | 0
| HOLYWELL T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.18917 | 0.16966 | 0.15731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18917 | 0.16966 | 0.15731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOOTON MAIN T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HUNTS CROSS T1 / KENTON RD T1 / WOODEND AVE T1 / WOOLTON T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HUYTON HEY RD T1 / WILSON RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IFTON T1 / IFTON T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.5172 | 7.4755 | 7.4894 | 7.4696 | 7.4239 | 7.4051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5172 | 7.4755 | 7.4894 | 7.4696 | 7.4239 | 7.4051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ILFORDS T1 / KNUTSFORD T1 / MOBBERLEY T1 / RADBROKE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 1.5195 | 1.4001 | 1.4203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5195 | 1.4001 | 1.4203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IVY ST (SOUTHPORT) T1 / KENSINGTON RD T1 / MARKET ST T1 / SOUTHPORT T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 3.1744 | 3.0375 | 3.0406 | 3.1164 | 3.125 | 3.1749 | 3.2231 | 3.2811 | 3.3364 | 3.4063 | 3.4647 | 3.7781 | 4.1837 | 3.8494 | 3.1846 | 3.1744 | 3.0375 | 3.0406 | 3.1164 | 3.125 | 3.1749 | 3.2231 | 3.2811 | 3.3364 | 3.4063 | 3.4647 | 3.7781 | 4.1837 | 3.8494 | 3.1846
| IVY ST T1 / LLYSFAEN RD T1 / OLD MILL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| JOHNSTOWN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.6097 | 7.6054 | 7.6475 | 7.7163 | 7.7524 | 7.8221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6097 | 7.6054 | 7.6475 | 7.7163 | 7.7524 | 7.8221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KELCO T1 / NEWS INTERNATIONAL T1 / NEWS INTERNATIONAL T2 / PALCO T1 / SOUTHDENE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KINGSLAND 33 T1 / SAFEWAY T1 / WOOLSTON T1 / WOOLSTON T2 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 3.5772 | 3.2425 | 3.1893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5772 | 3.2425 | 3.1893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KINNERTON T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 9.9817 | 9.9998 | 7.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9817 | 9.9998 | 7.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KIRKBY CENTRAL T1 / NORTHWOOD T1 / TOWER HILL (BANK LA) T1 / WESTVALE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KNOWSLEY T1 / MARLED HEY T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KNUTSFORD T2 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 1.3618 | 1.2903 | 1.3013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3618 | 1.2903 | 1.3013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LCWW HUNTINGTON T1 / LCWW HUNTINGTON T2 | 7 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEA GREEN T1 / PILKINGTONS HO T1 / RAVENHEAD RETAIL PK T1 / SOMERFIELD DISTRIBUTION T1 | 11 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEGACY LOCAL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 4.1997 | 4.1513 | 4.1515 | 4.1034 | 4.0498 | 3.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1997 | 4.1513 | 4.1515 | 4.1034 | 4.0498 | 3.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEIGHTON HOSP T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LIVERPOOL RD 33 T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 4.5272 | 4.49 | 4.5072 | 4.5161 | 4.4939 | 4.4922 | 4.505 | 4.5204 | 4.555 | 4.5759 | 4.5648 | 4.598 | 4.4702 | 3.969 | 3.4177 | 4.5272 | 4.49 | 4.5072 | 4.5161 | 4.4939 | 4.4922 | 4.505 | 4.5204 | 4.555 | 4.5759 | 4.5648 | 4.598 | 4.4702 | 3.969 | 3.4177
| LLAINGOCH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.14729 | 0.11329 | 0.14182 | 0.15468 | 0.20583 | 0.25464 | 0.31687 | 0.42079 | 0.53386 | 0.64671 | 0 | 0 | 0 | 0 | 0 | 0.14729 | 0.11329 | 0.14182 | 0.15468 | 0.20583 | 0.25464 | 0.31687 | 0.42079 | 0.53386 | 0.64671 | 0 | 0 | 0 | 0 | 0
| LLANARMON T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 9.5567 | 9.3432 | 9.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5567 | 9.3432 | 9.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANBEDROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.3024 | 8.7336 | 8.2876 | 7.87 | 7.1812 | 5.9115 | 5.3698 | 4.7468 | 4.178 | 3.6103 | 0 | 0 | 0 | 0 | 0 | 9.3024 | 8.7336 | 8.2876 | 7.87 | 7.1812 | 5.9115 | 5.3698 | 4.7468 | 4.178 | 3.6103 | 0 | 0 | 0 | 0 | 0
| LLANBERIS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 6.3392 | 6.1899 | 6.2169 | 6.2347 | 6.2319 | 6.2521 | 6.2641 | 6.2922 | 6.3155 | 6.3604 | 6.3541 | 6.381 | 6.2765 | 5.9663 | 5.5677 | 6.3392 | 6.1899 | 6.2169 | 6.2347 | 6.2319 | 6.2521 | 6.2641 | 6.2922 | 6.3155 | 6.3604 | 6.3541 | 6.381 | 6.2765 | 5.9663 | 5.5677
| LLANDDEUSANT T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDDU QUARRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 1.3397 | 1.2587 | 1.2376 | 1.1885 | 1.1263 | 1.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3397 | 1.2587 | 1.2376 | 1.1885 | 1.1263 | 1.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDEGFAN T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 6.4183 | 6.3917 | 6.3863 | 6.3496 | 6.3168 | 6.2704 | 6.237 | 6.1979 | 6.1747 | 6.1091 | 0 | 0 | 0 | 0 | 0 | 6.4183 | 6.3917 | 6.3863 | 6.3496 | 6.3168 | 6.2704 | 6.237 | 6.1979 | 6.1747 | 6.1091 | 0 | 0 | 0 | 0 | 0
| LLANDRINIO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 3.1122 | 2.9222 | 2.859 | 2.7549 | 2.6416 | 2.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1122 | 2.9222 | 2.859 | 2.7549 | 2.6416 | 2.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDUDNO T1 / LLANDUDNO T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 1.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDYFRYDOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.4398 | 7.2289 | 7.1467 | 7.0606 | 6.9807 | 6.7828 | 6.4121 | 5.9818 | 5.5994 | 4.9673 | 0 | 0 | 0 | 0 | 0 | 7.4398 | 7.2289 | 7.1467 | 7.0606 | 6.9807 | 6.7828 | 6.4121 | 5.9818 | 5.5994 | 4.9673 | 0 | 0 | 0 | 0 | 0
| LLANDYRNOG T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFAELOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 4.0298 | 4.0119 | 4.016 | 4.0421 | 4.0544 | 4.0766 | 4.1008 | 4.1273 | 4.1577 | 4.1885 | 0 | 0 | 0 | 0 | 0 | 4.0298 | 4.0119 | 4.016 | 4.0421 | 4.0544 | 4.0766 | 4.1008 | 4.1273 | 4.1577 | 4.1885 | 0 | 0 | 0 | 0 | 0
| LLANFAIR CAEREINION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 4.5122 | 4.4074 | 4.4033 | 4.3458 | 4.2907 | 4.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5122 | 4.4074 | 4.4033 | 4.3458 | 4.2907 | 4.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFAIR PG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.8798 | 7.8394 | 7.8381 | 7.8413 | 7.8512 | 7.8707 | 7.8813 | 7.9158 | 7.9623 | 8.0039 | 0 | 0 | 0 | 0 | 0 | 7.8798 | 7.8394 | 7.8381 | 7.8413 | 7.8512 | 7.8707 | 7.8813 | 7.9158 | 7.9623 | 8.0039 | 0 | 0 | 0 | 0 | 0
| LLANFAIRFECHAN T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 6.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFROTHEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.2174 | 9.1065 | 9.1265 | 9.1656 | 9.1904 | 9.2379 | 9.2703 | 9.3274 | 9.3818 | 9.4201 | 0 | 0 | 0 | 0 | 0 | 9.2174 | 9.1065 | 9.1265 | 9.1656 | 9.1904 | 9.2379 | 9.2703 | 9.3274 | 9.3818 | 9.4201 | 0 | 0 | 0 | 0 | 0
| LLANFWROG T1 / RUTHIN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFYLLIN T1 / LLANFYLLIN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANGAFFO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.5698 | 7.3542 | 7.2927 | 7.2038 | 7.1001 | 7.0289 | 6.9546 | 6.8647 | 6.7694 | 6.6285 | 0 | 0 | 0 | 0 | 0 | 7.5698 | 7.3542 | 7.2927 | 7.2038 | 7.1001 | 7.0289 | 6.9546 | 6.8647 | 6.7694 | 6.6285 | 0 | 0 | 0 | 0 | 0
| LLANGEFNI IND EST T1 / LLANGEFNI IND EST T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 1.4523 | 1.2393 | 1.1577 | 1.1164 | 1.0874 | 1.0556 | 1.0344 | 0.97687 | 0.85728 | 0.24818 | 0 | 0 | 0 | 0 | 0 | 1.4523 | 1.2393 | 1.1577 | 1.1164 | 1.0874 | 1.0556 | 1.0344 | 0.97687 | 0.85728 | 0.24818 | 0 | 0 | 0 | 0 | 0
| LLANGEFNI T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.2298 | 10.2056 | 10.2047 | 10.2148 | 10.21 | 10.2324 | 10.2361 | 10.2471 | 10.2587 | 9.6569 | 0 | 0 | 0 | 0 | 0 | 10.2298 | 10.2056 | 10.2047 | 10.2148 | 10.21 | 10.2324 | 10.2361 | 10.2471 | 10.2587 | 9.6569 | 0 | 0 | 0 | 0 | 0
| LLANGOLLEN T1 / LLANGOLLEN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.2397 | 0.19069 | 0.20005 | 0.17669 | 0.1375 | 0.12104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2397 | 0.19069 | 0.20005 | 0.17669 | 0.1375 | 0.12104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANIDLOES T1 / LLANIDLOES T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANILAR T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 1.9173 | 1.7161 | 1.6451 | 1.5651 | 1.4897 | 1.4052 | 1.3549 | 1.2935 | 1.225 | 1.0755 | 0.92676 | 0.68487 | 0 | 0 | 0 | 1.9173 | 1.7161 | 1.6451 | 1.5651 | 1.4897 | 1.4052 | 1.3549 | 1.2935 | 1.225 | 1.0755 | 0.92676 | 0.68487 | 0 | 0 | 0
| LLANRWST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 7.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANSANNAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 9.8467 | 9.4987 | 9.4223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8467 | 9.4987 | 9.4223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANSILIN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 8.4982 | 8.2733 | 8.2022 | 8.1063 | 8.013 | 7.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4982 | 8.2733 | 8.2022 | 8.1063 | 8.013 | 7.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLYNCLYS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9777 | 6.9905 | 7.0172 | 7.0114 | 7.0212 | 7.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9777 | 6.9905 | 7.0172 | 7.0114 | 7.0212 | 7.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LORD ST T1 / MARSHSIDE T1 / MULLARDS BALMORAL DV T1 / SOUTHPORT T2 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 3.8394 | 3.183 | 3.0827 | 2.9862 | 2.8442 | 2.7227 | 2.6014 | 2.543 | 2.4921 | 2.3606 | 2.1078 | 1.5413 | 0 | 0 | 0 | 3.8394 | 3.183 | 3.0827 | 2.9862 | 2.8442 | 2.7227 | 2.6014 | 2.543 | 2.4921 | 2.3606 | 2.1078 | 1.5413 | 0 | 0 | 0
| LOSTOCK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LOSTOCK TRIANGLE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 9.1922 | 9.1982 | 7.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1922 | 9.1982 | 7.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LOWER BEBINGTON T1 / NEW FERRY T1 / SPITAL T1 / UNILEVER RESEARCH T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LUGSDALE T1 / PILK SULLIVAN T1 / PILK SULLIVAN T2 / USAC T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 2.0978 | 2.0934 | 2.1372 | 2.0331 | 0 | 1.9267 | 1.8632 | 1.7955 | 1.7369 | 1.6889 | 1.7326 | 1.8247 | 1.6619 | 1.3255 | 0 | 2.0978 | 2.0934 | 2.1372 | 2.0331 | 0 | 1.9267 | 1.8632 | 1.7955 | 1.7369 | 1.6889 | 1.7326 | 1.8247 | 1.6619 | 1.3255
| LYMM T1 / WHITELEGGS LA T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 1.2072 | 1.1096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2072 | 1.1096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MACHYNLLETH T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 3.2828 | 3.2835 | 3.309 | 3.3678 | 3.3976 | 3.4705 | 3.5364 | 3.6194 | 3.7353 | 3.8256 | 3.9094 | 4.123 | 4.2647 | 4.0208 | 3.7712 | 3.2828 | 3.2835 | 3.309 | 3.3678 | 3.3976 | 3.4705 | 3.5364 | 3.6194 | 3.7353 | 3.8256 | 3.9094 | 4.123 | 4.2647 | 4.0208 | 3.7712
| MACHYNLLETH T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 4.3976 | 4.0991 | 3.9784 | 3.8959 | 3.802 | 3.7049 | 3.6246 | 3.5302 | 3.4379 | 3.2967 | 3.16 | 2.857 | 2.5429 | 1.0987 | 0 | 4.3976 | 4.0991 | 3.9784 | 3.8959 | 3.802 | 3.7049 | 3.6246 | 3.5302 | 3.4379 | 3.2967 | 3.16 | 2.857 | 2.5429 | 1.0987 | 0
| MAELOR CREAMERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 9.3797 | 9.1469 | 9.06 | 8.9745 | 8.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3797 | 9.1469 | 9.06 | 8.9745 | 8.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MAENTWROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.1949 | 8.9752 | 8.9028 | 8.8489 | 8.7894 | 8.7437 | 8.7292 | 8.6779 | 8.6629 | 8.5629 | 0 | 0 | 0 | 0 | 0 | 9.1949 | 8.9752 | 8.9028 | 8.8489 | 8.7894 | 8.7437 | 8.7292 | 8.6779 | 8.6629 | 8.5629 | 0 | 0 | 0 | 0 | 0
| MAES-Y-CLAWDD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 5.9347 | 5.8969 | 5.9036 | 5.9425 | 5.9323 | 5.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9347 | 5.8969 | 5.9036 | 5.9425 | 5.9323 | 5.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MANOD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.7729 | 2.599 | 2.5322 | 2.4782 | 2.4157 | 2.3987 | 2.3608 | 2.2915 | 2.2558 | 2.1311 | 0 | 0 | 0 | 0 | 0 | 2.7729 | 2.599 | 2.5322 | 2.4782 | 2.4157 | 2.3987 | 2.3608 | 2.2915 | 2.2558 | 2.1311 | 0 | 0 | 0 | 0 | 0
| MANOR PK T1 / NORTON CHAINS T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 2.0378 | 2.0585 | 2.2108 | 2.3767 | 2.3574 | 2.395 | 2.4632 | 2.5529 | 2.6075 | 2.5043 | 2.5965 | 3.1947 | 3.9584 | 4.3981 | 4.1659 | 2.0378 | 2.0585 | 2.2108 | 2.3767 | 2.3574 | 2.395 | 2.4632 | 2.5529 | 2.6075 | 2.5043 | 2.5965 | 3.1947 | 3.9584 | 4.3981 | 4.1659
| MDHB EGERTON DOCK T1 / MDHB EGERTON DOCK T2 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MERE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.9497 | 6.9513 | 6.9921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9497 | 6.9513 | 6.9921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MERES EDGE T1 / MERES EDGE T2 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 10.4053 | 8.7145 | 3.9691 | 10.4049 | 10.4236 | 10.4445 | 10.4628 | 10.4848 | 10.5505 | 10.5816 | 10.5875 | 10.6294 | 10.3213 | 9.3896 | 8.3013 | 10.4053 | 8.7145 | 3.9691 | 10.4049 | 10.4236 | 10.4445 | 10.4628 | 10.4848 | 10.5505 | 10.5816 | 10.5875 | 10.6294 | 10.3213 | 9.3896 | 8.3013
| MIDDLEWICH T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MIDPOINT POCHIN WAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 8.9122 | 8.8996 | 7.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9122 | 8.8996 | 7.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MILFORD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MINFFORDD T1 / PARC BRYN CEGIN T1 / PARC BRYN CEGIN T2 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 1.0717 | 1.047 | 1.0607 | 1.0573 | 1.0692 | 1.0789 | 1.1054 | 1.1186 | 1.1629 | 1.1831 | 1.1834 | 1.2721 | 1.2333 | 1.0258 | 0.52794 | 1.0717 | 1.047 | 1.0607 | 1.0573 | 1.0692 | 1.0789 | 1.1054 | 1.1186 | 1.1629 | 1.1831 | 1.1834 | 1.2721 | 1.2333 | 1.0258 | 0.52794
| MOCHDRE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9472 | 6.7659 | 6.7018 | 6.6661 | 6.599 | 6.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9472 | 6.7659 | 6.7018 | 6.6661 | 6.599 | 6.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MONA T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 5.2973 | 3.4713 | 4.011 | 4.1531 | 4.1814 | 4.2113 | 4.1236 | 4.0635 | 3.9879 | 3.7744 | 0 | 0 | 0 | 0 | 0 | 5.2973 | 3.4713 | 4.011 | 4.1531 | 4.1814 | 4.2113 | 4.1236 | 4.0635 | 3.9879 | 3.7744 | 0 | 0 | 0 | 0 | 0
| MONSANTO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MORDA T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 8.8697 | 4.7072 | 4.9118 | 5.2832 | 5.5169 | 5.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8697 | 4.7072 | 4.9118 | 5.2832 | 5.5169 | 5.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MORGANITE CERAMICS T1 / PLYMYARD T2 / VAUXHALL NORTH RD T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MORRISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 7.3172 | 7.279 | 7.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3172 | 7.279 | 7.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NANTWICH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NANT-Y-GAMAR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 0.35917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NEVILL ST T1 / OCEAN PLAZA T1 / YORK RD T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 1.9769 | 1.9031 | 1.9027 | 1.948 | 1.9153 | 1.8998 | 1.9028 | 1.8753 | 1.8684 | 1.8432 | 1.8315 | 1.908 | 2.0305 | 1.7918 | 1.37 | 1.9769 | 1.9031 | 1.9027 | 1.948 | 1.9153 | 1.8998 | 1.9028 | 1.8753 | 1.8684 | 1.8432 | 1.8315 | 1.908 | 2.0305 | 1.7918 | 1.37
| NEW BRIGHTON T1 / SEAVIEW RD T2 / WALLASEY T1 / WALLASEY VILLAGE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NEWHALL T1 / NEWHALL T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NORTH WALES PAPER T1 / NORTH WALES PAPER T2 / WOODFIELD AVE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 3.2592 | 3.1468 | 3.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2592 | 3.1468 | 3.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NORTH WEST WATER CAMPUS T1 / NORTH WEST WATER CAMPUS T2 / OMEGA T1 / OMEGA T2 / ORION BOULEVARD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OPTICAL FIBRES T1 / SHOTWICK T1 / WALBRO T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | Yes | 2037 | 1.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ORB CL T1 / STONEBRIDGE LA T1 / STONEBRIDGE LA T2 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 0.16693 | 0.088772 | 0.086474 | 0.079955 | 0.018124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16693 | 0.088772 | 0.086474 | 0.079955 | 0.018124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ORFORD T1 / PADGATE T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.1822 | 1.2178 | 1.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1822 | 1.2178 | 1.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OTIS ELEVATOR T1 / ST IVEL FOODS T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OVERTON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.4847 | 0.33557 | 0.20765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4847 | 0.33557 | 0.20765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PANDY T1 / PANDY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 1.0672 | 0.90408 | 0.86709 | 0.76414 | 0.65759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0672 | 0.90408 | 0.86709 | 0.76414 | 0.65759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PARC CYBI T1 / PARC CYBI T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.57979 | 0.57332 | 0.58662 | 0.62703 | 0.63894 | 0.66794 | 0.69122 | 0.70569 | 0.73971 | 0.75164 | 0 | 0 | 0 | 0 | 0 | 0.57979 | 0.57332 | 0.58662 | 0.62703 | 0.63894 | 0.66794 | 0.69122 | 0.70569 | 0.73971 | 0.75164 | 0 | 0 | 0 | 0 | 0
| PARC MENAI T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 7.0417 | 7.0392 | 7.0505 | 7.0355 | 7.0232 | 7.0141 | 7.027 | 7.0181 | 7.0316 | 7.0579 | 7.0554 | 7.1015 | 7.128 | 7.0016 | 6.7954 | 7.0417 | 7.0392 | 7.0505 | 7.0355 | 7.0232 | 7.0141 | 7.027 | 7.0181 | 7.0316 | 7.0579 | 7.0554 | 7.1015 | 7.128 | 7.0016 | 6.7954
| PEBLIC MILLS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PENMAENMAWR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 9.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PENTRAETH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.4523 | 10.4153 | 10.4054 | 10.3993 | 10.3836 | 10.3727 | 10.3326 | 10.3134 | 10.2861 | 9.6569 | 0 | 0 | 0 | 0 | 0 | 10.4523 | 10.4153 | 10.4054 | 10.3993 | 10.3836 | 10.3727 | 10.3326 | 10.3134 | 10.2861 | 9.6569 | 0 | 0 | 0 | 0 | 0
| PEN-Y-GROES T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 3.2812 | 2.8463 | 2.9219 | 2.9339 | 2.9523 | 2.9686 | 2.9636 | 2.9868 | 3.0051 | 3.024 | 2.9879 | 2.9438 | 2.7763 | 2.4289 | 1.7728 | 3.2812 | 2.8463 | 2.9219 | 2.9339 | 2.9523 | 2.9686 | 2.9636 | 2.9868 | 3.0051 | 3.024 | 2.9879 | 2.9438 | 2.7763 | 2.4289 | 1.7728
| PILKINGTONS T1 / PILKINGTONS T2 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.53917 | 0.30689 | 0.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53917 | 0.30689 | 0.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| POINT OF AYR COLLIERY T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.45167 | 0.4261 | 0.44073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45167 | 0.4261 | 0.44073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PORTHMADOG T1 / PORTHMADOG T2 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.86741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PREES T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 9.8447 | 9.4557 | 9.2572 | 9.0112 | 8.7774 | 8.582 | 8.4584 | 8.3534 | 8.3522 | 8.1244 | 7.8238 | 7.3734 | 7.2049 | 6.2642 | 4.9878 | 9.8447 | 9.4557 | 9.2572 | 9.0112 | 8.7774 | 8.582 | 8.4584 | 8.3534 | 8.3522 | 8.1244 | 7.8238 | 7.3734 | 7.2049 | 6.2642 | 4.9878
| PRIMROSE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.6447 | 6.6282 | 6.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6447 | 6.6282 | 6.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PWLLHELI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 7.6949 | 7.6552 | 7.6528 | 7.6654 | 7.6674 | 7.699 | 7.7161 | 7.7377 | 7.7691 | 7.7985 | 0 | 0 | 0 | 0 | 0 | 7.6949 | 7.6552 | 7.6528 | 7.6654 | 7.6674 | 7.699 | 7.7161 | 7.7377 | 7.7691 | 7.7985 | 0 | 0 | 0 | 0 | 0
| RADWAY GREEN T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RAVEN SQUARE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFORM ST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 10.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHM FOODS LTD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHOSLAN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.9369 | 9.9373 | 9.9683 | 10.0216 | 10.0841 | 10.1589 | 10.2463 | 10.3469 | 10.4627 | 10.5559 | 0 | 0 | 0 | 0 | 0 | 9.9369 | 9.9373 | 9.9683 | 10.0216 | 10.0841 | 10.1589 | 10.2463 | 10.3469 | 10.4627 | 10.5559 | 0 | 0 | 0 | 0 | 0
| RHUDDLAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 6.7042 | 6.6307 | 6.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7042 | 6.6307 | 6.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHYDLYDAN T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 1.5673 | 1.5684 | 1.582 | 1.5821 | 1.5687 | 1.5823 | 1.5867 | 1.5894 | 1.6186 | 1.639 | 1.6372 | 1.6584 | 1.6409 | 1.4704 | 1.2642 | 1.5673 | 1.5684 | 1.582 | 1.5821 | 1.5687 | 1.5823 | 1.5867 | 1.5894 | 1.6186 | 1.639 | 1.6372 | 1.6584 | 1.6409 | 1.4704 | 1.2642
| RHYD-Y-FOEL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RINGWAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.5372 | 6.3024 | 6.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5372 | 6.3024 | 6.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RIVALS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 3.6424 | 3.4559 | 3.3713 | 3.2864 | 4.413 | 4.3607 | 4.3489 | 4.3629 | 4.389 | 4.3848 | 0 | 0 | 0 | 0 | 0 | 3.6424 | 3.4559 | 3.3713 | 3.2864 | 4.413 | 4.3607 | 4.3489 | 4.3629 | 4.389 | 4.3848 | 0 | 0 | 0 | 0 | 0
| ROLLS ROYCE T1 / ROLLS ROYCE T2 / ROLLS ROYCE T3 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROSSETT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 8.8397 | 8.9253 | 9.1647 | 9.3523 | 9.3535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8397 | 8.9253 | 9.1647 | 9.3523 | 9.3535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROYAL INSURANCE (NEW QUAY) T1 / ROYAL INSURANCE (NEW QUAY) T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RUABON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALTNEY T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SANDBACH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHAWBURY T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMALLWOOD T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SNOWHILL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ST ASAPH BUSINESS PK T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 10.2743 | 10.1799 | 10.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2743 | 10.1799 | 10.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ST HELENS RD T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0.21917 | 0.18652 | 0.19567 | 0.20855 | 0.20484 | 0.22224 | 0.2367 | 0.27001 | 0.3008 | 0.32574 | 0.33806 | 0.40595 | 0.38411 | 0.21303 | 0 | 0.21917 | 0.18652 | 0.19567 | 0.20855 | 0.20484 | 0.22224 | 0.2367 | 0.27001 | 0.3008 | 0.32574 | 0.33806 | 0.40595 | 0.38411 | 0.21303 | 0
| STAPELEY T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TACO PLASTICS T1 / TACO PLASTICS T2 / UNITED PERIPHERALS T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 1.8552 | 1.7947 | 1.8046 | 1.9266 | 1.9243 | 1.9567 | 1.9834 | 2.0028 | 2.0041 | 2.0341 | 2.0391 | 2.2142 | 2.4496 | 0 | 0 | 1.8552 | 1.7947 | 1.8046 | 1.9266 | 1.9243 | 1.9567 | 1.9834 | 2.0028 | 2.0041 | 2.0341 | 2.0391 | 2.2142 | 2.4496 | 0 | 0
| TARPORLEY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.0672 | 7.0292 | 7.0429 | 7.0053 | 6.9754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0672 | 7.0292 | 7.0429 | 7.0053 | 6.9754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TARVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRYWERYN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 4.6274 | 4.1395 | 4.1656 | 4.1766 | 4.1849 | 4.2038 | 4.1886 | 4.0782 | 3.9669 | 3.6314 | 0 | 0 | 0 | 0 | 0 | 4.6274 | 4.1395 | 4.1656 | 4.1766 | 4.1849 | 4.2038 | 4.1886 | 4.0782 | 3.9669 | 3.6314 | 0 | 0 | 0 | 0 | 0
| TWYFORDS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TYWYN T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 7.1823 | 7.1711 | 7.209 | 7.2614 | 7.2839 | 7.3296 | 7.3747 | 7.4228 | 7.5345 | 7.5976 | 7.6009 | 7.6776 | 7.4527 | 7.0632 | 6.3864 | 7.1823 | 7.1711 | 7.209 | 7.2614 | 7.2839 | 7.3296 | 7.3747 | 7.4228 | 7.5345 | 7.5976 | 7.6009 | 7.6776 | 7.4527 | 7.0632 | 6.3864
| WAENFAWR T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 9.1077 | 8.6553 | 8.6682 | 8.6765 | 8.6978 | 8.7209 | 8.7543 | 8.7796 | 8.843 | 8.8742 | 8.781 | 8.4463 | 8.0802 | 4.9341 | 1.4208 | 9.1077 | 8.6553 | 8.6682 | 8.6765 | 8.6978 | 8.7209 | 8.7543 | 8.7796 | 8.843 | 8.8742 | 8.781 | 8.4463 | 8.0802 | 4.9341 | 1.4208
| WELSHPOOL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEM EAST T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEM T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WERVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEST FELTON T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 7.7672 | 7.6222 | 7.5838 | 7.5637 | 7.5023 | 7.4315 | 7.3744 | 7.2518 | 7.1675 | 6.898 | 6.3852 | 5.4816 | 4.9474 | 1.5622 | 0 | 7.7672 | 7.6222 | 7.5838 | 7.5637 | 7.5023 | 7.4315 | 7.3744 | 7.2518 | 7.1675 | 6.898 | 6.3852 | 5.4816 | 4.9474 | 1.5622 | 0
| WESTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WHEELOCK T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WHITCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 5.7972 | 5.7159 | 5.7023 | 5.6292 | 5.5532 | 5.4769 | 5.4236 | 5.357 | 5.3119 | 5.2592 | 5.1764 | 5.0364 | 4.5804 | 3.8716 | 2.8439 | 5.7972 | 5.7159 | 5.7023 | 5.6292 | 5.5532 | 5.4769 | 5.4236 | 5.357 | 5.3119 | 5.2592 | 5.1764 | 5.0364 | 4.5804 | 3.8716 | 2.8439
| WIMPEYS PANT QUARRY T1 / WIMPEYS PANT QUARRY T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0.68417 | 0.49927 | 0.45066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68417 | 0.49927 | 0.45066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WINCHAM T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 6.5697 | 6.5601 | 6.5672 | 6.5612 | 6.4824 | 6.424 | 6.3724 | 6.3204 | 6.2856 | 6.2433 | 6.2229 | 6.1827 | 6.0889 | 0 | 0 | 6.5697 | 6.5601 | 6.5672 | 6.5612 | 6.4824 | 6.424 | 6.3724 | 6.3204 | 6.2856 | 6.2433 | 6.2229 | 6.1827 | 6.0889 | 0 | 0
| WISTASTON HALL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WRENBURY FRITH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| YOCKINGS GATE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| YSBYTY GLAN CLWYD T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 5.7067 | 5.6777 | 5.6825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7067 | 5.6777 | 5.6825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Groups | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 33 | SWANSEA NORTH | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 6.8433 | 4.6363 | 2.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.2166 | 23.1814 | 11.1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 33 | TRAWSFYNYDD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 33 | CELLARHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 33 | KIRKBY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 33 | KIRKBY | Yes | 2037 | 19.5203 | 18.3924 | 17.066 | 15.3461 | 14.0287 | 12.6637 | 11.2822 | 10.6652 | 10.1353 | 9.4858 | 8.9177 | 7.6636 | 6.0362 | 4.2869 | 2.5274 | 65.994 | 63.9111 | 61.8217 | 58.7441 | 57.6272 | 56.5059 | 55.3923 | 53.326 | 50.6767 | 47.429 | 44.5884 | 38.3178 | 30.1811 | 21.4346 | 12.6369
| AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 33 | KIRKBY | Yes | 2037 | 3.6894 | 3.6258 | 3.3759 | 2.7552 | 2.5318 | 2.2675 | 1.932 | 1.3488 | 0.7969 | 0.119 | 0 | 0 | 0 | 0 | 0 | 18.4472 | 18.1289 | 16.8793 | 13.7762 | 12.6592 | 11.3374 | 9.6601 | 6.7442 | 3.9845 | 0.59501 | 0 | 0 | 0 | 0 | 0
| CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 5.341 | 2.9883 | 1.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.7049 | 14.9414 | 7.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 33 | KIRKBY | Yes | 2037 | 13.3525 | 12.4245 | 11.4461 | 10.0447 | 9.1198 | 8.2069 | 7.7714 | 6.8811 | 6.0645 | 5.1819 | 4.5173 | 2.9321 | 1.6053 | 0 | 0 | 63.7423 | 61.7169 | 57.2307 | 50.2234 | 45.5991 | 41.0345 | 38.8568 | 34.4055 | 30.3226 | 25.9094 | 22.5865 | 14.6604 | 8.0267 | 0 | 0
| AMLWCH GT1 / CAERGEILIOG GT1 | 33 | WYLFA | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 10.8137 | 9.6654 | 9.316 | 8.2163 | 7.7611 | 7.2541 | 6.5798 | 5.7892 | 4.4804 | 3.4606 | 3.018 | 1.6226 | 1.5398 | 0 | 0 | 54.0684 | 48.327 | 46.5801 | 41.0817 | 38.8057 | 36.2707 | 32.8988 | 28.9461 | 22.4021 | 17.3032 | 15.0899 | 8.1131 | 7.6992 | 0 | 0
| BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 33 | RAINHILL | Yes | 2037 | 0 | 8.4832 | 3.6794 | 2.2133 | 0.88714 | 0 | 1.2498 | 4.1418 | 5.7867 | 5.4805 | 5.6564 | 7.3251 | 9.2878 | 9.5506 | 8.5876 | 0 | 31.1956 | 18.3971 | 11.0665 | 4.4357 | 0 | 6.249 | 20.7091 | 26.2181 | 25.0684 | 24.295 | 24.9779 | 25.1333 | 20.8286 | 11.6613
| HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 33 | BIRKENHEAD | Yes | 2037 | 5.9072 | 5.8565 | 5.78 | 5.5816 | 5.3841 | 5.0927 | 4.8098 | 4.5199 | 4.2155 | 3.9857 | 3.8084 | 3.4279 | 2.9507 | 2.0753 | 0.68745 | 29.5361 | 29.2825 | 28.8999 | 27.9082 | 26.9207 | 25.4637 | 24.0491 | 22.5993 | 21.0774 | 19.9283 | 19.0421 | 17.1393 | 14.7536 | 10.3765 | 3.4372
| BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 33 | LEGACY | Yes | 2037 | 24.1408 | 19.178 | 13.8366 | 7.8787 | 2.3189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.5349 | 95.8898 | 69.1832 | 39.3935 | 11.5944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 33 | CAPENHURST | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 33 | FRODSHAM - INCE | Yes | 2037 | 10.4504 | 9.8515 | 9.3851 | 8.5369 | 8.1013 | 7.7502 | 7.0523 | 6.7854 | 6.2978 | 6.0689 | 6.1278 | 6.2953 | 7.5701 | 6.3876 | 2.2696 | 34.6145 | 33.0822 | 30.8018 | 27.7165 | 25.4909 | 23.5774 | 21.086 | 21.3291 | 21.0047 | 20.9676 | 24.3114 | 25.992 | 28.9231 | 27.5936 | 11.3479
| BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BANGOR GT2 / CAERNARFON GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 13.9608 | 9.2573 | 8.2245 | 5.9616 | 5.4455 | 4.1641 | 3.0572 | 1.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9608 | 9.2573 | 8.2245 | 5.9616 | 5.4455 | 4.1641 | 3.0572 | 1.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 4.2875 | 1.7721 | 0.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4885 | 5.1693 | 3.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OSWESTRY GT5 / WHITCHURCH GT1 | 33 | LEGACY | Yes | 2037 | 39.3925 | 38.5916 | 37.3081 | 35.162 | 33.2769 | 31.1505 | 29.3862 | 27.7551 | 25.599 | 23.4769 | 21.5514 | 16.3998 | 12.7229 | 4.4666 | 0 | 126.6824 | 124.3536 | 121.0245 | 114.2722 | 108.7504 | 102.1749 | 95.6685 | 88.7421 | 80.1833 | 71.2968 | 63.0729 | 42.5372 | 26.6634 | 4.4666 | 0
| GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PRENTON GRID GT1 / ROCK FERRY GT1 | 33 | BIRKENHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 33 | FRODSHAM - INCE | Yes | 2037 | 5.2937 | 1.7429 | 0.79382 | 2.081 | 3.9246 | 5.6432 | 6.643 | 8.1264 | 9.2093 | 8.7845 | 8.7132 | 9.3049 | 9.4031 | 4.8668 | 0.28461 | 20.8002 | 8.7145 | 3.9691 | 10.0876 | 12.0784 | 13.8951 | 14.8462 | 16.237 | 16.318 | 14.5221 | 13.6379 | 13.0687 | 10.5667 | 4.8668 | 0.28461
| BOOTLE GT1 / LITHERLAND GT1A | 33 | KIRKBY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 33 | CAPENHURST | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 33 | LEGACY | Yes | 2037 | 16.6627 | 9.4217 | 1.5278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6627 | 9.4217 | 1.5278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SANKEY BRIDGES GT3 / WARRINGTON GT5 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 33 | RAINHILL | Yes | 2037 | 6.6565 | 3.9709 | 1.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6565 | 3.9709 | 1.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 2.9733 | 1.9328 | 1.1983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8663 | 9.6639 | 5.9914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMBOROUGH GT3 / ROCK FERRY GT2 | 33 | BIRKENHEAD | Yes | 2037 | 7.0083 | 4.5514 | 3.1328 | 1.6594 | 0.45094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0083 | 4.5514 | 3.1328 | 1.6594 | 0.45094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 33 | BIRKENHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 10.8137 | 4.5294 | 1.4465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0684 | 22.6471 | 7.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 4.217 | 11.5263 | 9.5621 | 7.1602 | 6.3181 | 4.5777 | 2.6916 | 1.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.217 | 11.5263 | 9.5621 | 7.1602 | 6.3181 | 4.5777 | 2.6916 | 1.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Low Scenario (Gen)
Generation Headroom (MW)
Return to Contents |  |  |  | Subject to upstream constraints beyond our network boundary (Yes/No) (See section 7.3 of the methodology statement) | Expected upsteam capacity release date (provided by National Grid Electricity Transmission) | Synchronous | [14 empty] | Fully Converted
| Group Name | Voltage (kV) | Grid / GSP Group |  |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050
Primary Groups | ABERDYFI T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 7.0173 | 6.9919 | 6.9802 | 7.0087 | 7.0427 | 7.0404 | 7.0435 | 7.0574 | 7.0993 | 7.115 | 7.1274 | 7.1509 | 7.0862 | 6.8651 | 6.6933 | 7.0173 | 6.9919 | 6.9802 | 7.0087 | 7.0427 | 7.0404 | 7.0435 | 7.0574 | 7.0993 | 7.115 | 7.1274 | 7.1509 | 7.0862 | 6.8651 | 6.6933
| ABERGELE T1 / PENSARN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 1.6617 | 1.5384 | 1.5329 | 1.4995 | 1.5648 | 1.5378 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 1.3847 | 0 | 1.6617 | 1.5384 | 1.5329 | 1.4995 | 1.5648 | 1.5378 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 1.3847 | 0
| ABERSOCH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028338 | 0 | 0 | 0
| ABERYSTWYTH T1 / NORTH RD T1 / PARC-Y-LLYN T1 / PARC-Y-LLYN T2 / U C WALES T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 5.1952 | 5.1952 | 5.068 | 5.0986 | 5.1683 | 5.1428 | 5.1199 | 5.0923 | 5.0632 | 5.0275 | 4.9973 | 4.896 | 4.7276 | 4.554 | 4.3813 | 5.4223 | 5.201 | 5.068 | 5.0986 | 5.3715 | 5.4422 | 5.5723 | 5.6733 | 5.7171 | 5.7621 | 5.886 | 6.413 | 7.0216 | 6.6222 | 6.1153
| ACER AVE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACORNFIELD RD T1 / DICKINSONS T1 / HAMMOND RD T1 / KODAK T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIGBURTH VALE T1 / IVY AVE T1 / MATHER AVE T1 / MOSSLEY HILL T1 / WAVERTREE T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AINSDALE T1 / PINFOLD LA T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 0.49443 | 0.40328 | 0.38631 | 0.42157 | 0.43237 | 0.33024 | 0.26689 | 0.19623 | 0.12685 | 0.046426 | 0.0017205 | 0 | 0 | 0 | 0 | 0.49443 | 0.40328 | 0.38631 | 0.42157 | 0.43237 | 0.33024 | 0.26689 | 0.19623 | 0.12685 | 0.046426 | 0.0017205 | 0 | 0 | 0 | 0
| AINTREE LOCAL T1 / OLD ROAN T1 / WANGO LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 2.3344 | 2.1778 | 2.0853 | 2.1308 | 2.2139 | 2.1426 | 2.1216 | 2.0895 | 2.004 | 1.9803 | 1.9777 | 1.9396 | 0 | 0 | 0 | 2.3344 | 2.1778 | 2.0853 | 2.1308 | 2.2139 | 2.1426 | 2.1216 | 2.0895 | 2.004 | 1.9803 | 1.9777 | 1.9396 | 0 | 0 | 0
| AIRBUS T1 / BROUGHTON RETAIL PARK T1 / MIXALLOY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 1.3332 | 0.44497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3332 | 0.44497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIRPORT T1 / ALDERWOOD AVE (CROYDE RD) T1 / HAREFIELD RD T1 / METAL BOX (SPEKE) T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALBERT DOCK T1 / KINGS DOCK T1 / KINGS DOCK T2 / WAPPING T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALLERTON T1 / ECP WEST-BANKS RD T1 / GARSTON T1 / WEAVER IND EST T1 / YEW TREE RD T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALMATEX T1 / ST HELENS WWTW T1 / WATERY LA T2 / ex DELTA METALS T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0.24685 | 0.24685 | 0.24685 | 0.24685 | 0.24685 | 0.22611 | 0.20504 | 0.18816 | 0.16667 | 0 | 0 | 0.099771 | 0.048265 | 0.013198 | 0 | 1.2343 | 1.2343 | 1.2343 | 1.2343 | 1.2343 | 1.1306 | 1.0252 | 0.94078 | 0.83335 | 0 | 0 | 0.49886 | 0.24133 | 0.065991 | 0
| ALMONDS TURN T1 / ATLANTIC COMPLEX T1 / GIRO T1 / MIDLAND BANK T1 / NETHERTON T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 1.0494 | 0 | 0 | 0 | 0 | 0.061353 | 0.041328 | 0 | 0 | 0 | 0 | 0 | 0.75277 | 0.54474 | 0 | 1.0494 | 0 | 0 | 0 | 0 | 0.061353 | 0.041328 | 0 | 0 | 0 | 0 | 0 | 0.75277 | 0.54474 | 0
| ALPOCO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052918 | 0 | 0 | 0
| AMLWCH T1 / AMLWCH T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ANDERTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| APPLETON T1 / HORNSBRIDGE T1 / LUGSDALE T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 2.6374 | 2.5067 | 2.5052 | 2.5789 | 2.4207 | 2.3158 | 2.1791 | 2.0238 | 1.8823 | 1.7808 | 1.7688 | 1.474 | 0.28976 | 0 | 0 | 2.6374 | 2.5067 | 2.5052 | 2.5789 | 2.4207 | 2.3158 | 2.1791 | 2.0238 | 1.8823 | 1.7808 | 1.7688 | 1.474 | 0.28976 | 0
| ARROWE PK HOSP T1 / CHAMPION PLUGS T1 / CHAMPION PLUGS T2 / WOODCHURCH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097164 | 0.19832 | 0.24913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097164 | 0.19832 | 0.24913
| ARUNDEL T1 / GROVE PK T1 / WAVERTREE VALE T1 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASH RD T1 / KELLOGGS (WREXHAM) T1 / KELLOGGS (WREXHAM) T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 1.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASSOCIATED LEAD T1 / GREAT BOUGHTON T1 / PIPERS ASH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASTMOOR IND EST T1 / MACKAMAX T1 / MERSEY RD T1 / PICOW FARM RD T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ATHOL ST T1 / CHISENHALE ST T1 / SANDHILLS LA T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AUDLEM T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BALA T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.2554 | 9.1112 | 9.1404 | 9.2027 | 9.2206 | 9.2722 | 9.3264 | 9.3978 | 9.4673 | 9.5134 | 9.5872 | 7.0761 | 0 | 0 | 0 | 9.2554 | 9.1112 | 9.1404 | 9.2027 | 9.2206 | 9.2722 | 9.3264 | 9.3978 | 9.4673 | 9.5134 | 9.5872 | 7.0761 | 0 | 0 | 0
| BANASTRE RD T1 / DOVER RD T1 / GRANTHAM CL T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 2.1094 | 1.9119 | 1.8119 | 1.7471 | 1.7659 | 1.7172 | 1.6326 | 1.5644 | 1.457 | 1.3818 | 1.3358 | 1.4622 | 1.2229 | 0.22936 | 0 | 2.1094 | 1.9119 | 1.8119 | 1.7471 | 1.7659 | 1.7172 | 1.6326 | 1.5644 | 1.457 | 1.3818 | 1.3358 | 1.4622 | 1.2229 | 0.22936 | 0
| BANGOR HOSP T1 / BANGOR UNIVERSITY T1 / EITHINOG T1 / HIRAEL T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BARBAULD ST T1 / HORROCKS LA T1 / WARRINGTON CENTRAL T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.6497 | 1.5545 | 1.5107 | 1.5527 | 1.7374 | 1.8178 | 1.8245 | 1.8436 | 1.8754 | 0 | 0 | 0 | 2.2935 | 2.4871 | 0 | 1.6497 | 1.5545 | 1.5107 | 1.5527 | 1.7374 | 1.8178 | 1.8245 | 1.8436 | 1.8754 | 0 | 0 | 0 | 2.2935 | 2.4871 | 0
| BARMOUTH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.8134 | 9.423 | 9.46 | 9.5458 | 9.626 | 9.7216 | 9.7696 | 9.7965 | 9.8243 | 9.8269 | 9.8025 | 7.0761 | 0 | 0 | 0 | 9.8134 | 9.423 | 9.46 | 9.5458 | 9.626 | 9.7216 | 9.7696 | 9.7965 | 9.8243 | 9.8269 | 9.8025 | 7.0761 | 0 | 0 | 0
| BARNSTON T1 / GAYTON T1 / IRBY T1 / THINGWALL T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 4.6697 | 4.4362 | 4.3571 | 4.2791 | 4.3243 | 4.1928 | 4.1215 | 4.0702 | 3.9539 | 3.8341 | 3.8185 | 3.9752 | 3.7595 | 1.6647 | 0 | 4.6697 | 4.4362 | 4.3571 | 4.2791 | 4.3243 | 4.1928 | 4.1215 | 4.0702 | 3.9539 | 3.8341 | 3.8185 | 3.9752 | 3.7595 | 1.6647 | 0
| BASCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BASS CHARRINGTON T1 / BASS CHARRINGTON T2 / CLIFTON T1 / YKK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 2.5478 | 2.3363 | 2.1997 | 2.1587 | 2.3584 | 2.4678 | 2.484 | 2.4787 | 2.4095 | 2.3638 | 2.353 | 2.4566 | 2.5504 | 2.0985 | 1.2684 | 2.5478 | 2.3363 | 2.1997 | 2.1587 | 2.3584 | 2.4678 | 2.484 | 2.4787 | 2.4095 | 2.3638 | 2.353 | 2.4566 | 2.5504 | 2.0985 | 1.2684
| BATTERSBY LA T1 / RYLANDS ELDON ST T2 | 6 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEAUMARIS T1 / BEAUMARIS T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.2973 | 10.2732 | 10.2808 | 10.3507 | 10.3907 | 10.4328 | 10.4967 | 10.5368 | 10.5654 | 10.5939 | 10.6161 | 1.6089 | 0 | 0 | 0 | 10.2973 | 10.2732 | 10.2808 | 10.3507 | 10.3907 | 10.4328 | 10.4967 | 10.5368 | 10.5654 | 10.5939 | 10.6161 | 1.6089 | 0 | 0 | 0
| BEAUMONT ST T1 / DINGLE VALE T1 / LARK LA T1 / MDHB BRUNSWICK DOCK T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEDBURN DV T1 / BLUEBELL LA T1 / BROOKBRIDGE T1 / ECCLESTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEECH ST T1 / LISTER DV A T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEMROSE T1 / CARR LA EAST T1 / LUCAS (FAZAKERLEY) T1 / NORRIS GREEN T1 / WEST DERBY T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 3.6551 | 3.6523 | 3.649 | 3.619 | 3.5722 | 3.5111 | 3.4495 | 3.3741 | 3.305 | 3.223 | 3.1463 | 1.9396 | 0 | 0 | 0 | 5.2394 | 4.9354 | 4.7418 | 4.5858 | 4.6876 | 4.6513 | 4.6116 | 4.4478 | 4.2731 | 4.0915 | 4.0066 | 1.9396 | 0 | 0 | 0
| BENTINCK ST T1 / BENTINCK ST T2 / CHESTER ST T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BERSHAM COLLIERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 4.4247 | 4.3992 | 4.3786 | 4.3807 | 4.3993 | 4.3608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4247 | 4.3992 | 4.3786 | 4.3807 | 4.3993 | 4.3608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BERSHAM RD T1 / IND COOPE T1 / RHYD BROUGHTON LA T1 / TUTTLE ST T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 3.4097 | 3.1846 | 3.0438 | 3.0163 | 3.218 | 3.3392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4097 | 3.1846 | 3.0438 | 3.0163 | 3.218 | 3.3392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BETHESDA T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BETWS-Y-COED T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 9.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEWSEY T1 / OWEN ST T1 / RODNEY ST T1 / RYLANDS ELDON ST T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 3.7892 | 3.5654 | 3.4407 | 3.4731 | 3.7229 | 3.8234 | 3.9089 | 3.9302 | 3.9267 | 0 | 0 | 0 | 4.6522 | 4.3638 | 0 | 3.7892 | 3.5654 | 3.4407 | 3.4731 | 3.7229 | 3.8234 | 3.9089 | 3.9302 | 3.9267 | 0 | 0 | 0 | 4.6522 | 4.3638 | 0
| BIBBYS T1 / INLAND REVENUE OFFICES T1 / REGENT RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BICC HUYTON QUARRY T1 / TARBOCK T1 / WHISTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BICC WREXHAM T1 / MARCHWIEL T1 / WIE CENTRAL T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 2.7472 | 2.3808 | 2.2418 | 2.257 | 2.4658 | 2.5342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7472 | 2.3808 | 2.2418 | 2.257 | 2.4658 | 2.5342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BIRKENHEAD CENTRAL T1 / SINGLETON AVE T1 / TRANMERE T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ex BIXTETH ST T1 / LITTLEWOODS T1 / PALL MALL T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLACON T1 / COCOA BARRY T1 / CRANE BANK T1 / KNUTSFORD WAY T1 / TOWER WHARF T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLAENAU FFESTINIOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLUNDELL ST T1 / ROPEWALKS T1 / ST JAMES T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLUNDELLSANDS (NORTH) T1 / BLUNDELLSANDS (SOUTH) T1 / CROSBY T1 / KERSHAW AVE T1 / WATERLOO T2 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 3.6144 | 3.6116 | 3.6082 | 3.5709 | 3.5118 | 3.4365 | 3.3589 | 3.2755 | 3.1874 | 3.0907 | 2.999 | 2.6921 | 2.1449 | 1.5776 | 0 | 5.6869 | 5.3619 | 5.2712 | 5.1345 | 5.2327 | 5.0661 | 4.9674 | 4.8428 | 4.6603 | 4.4934 | 4.4544 | 4.4999 | 4.2419 | 2.5056 | 0
| BODFARI PRODUCERS T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOLTON ST T1 / GREEK ST T1 / HPO COPPERAS HILL T1 / OLDHAM PLACE T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GRID T1 / KELLOGGS T1 / PACIFIC RD T1 / WASHINGTON ST T1 / WATERLOO T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0025 | 0.52356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0025 | 0.52356 | 0
| BOOTLE GRID T2 / ORRELL MOUNT T1 / SCARISBRICK AVE T1 / TATTON RD T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1507 | 3.3419 | 3.4467 | 2.4933 | 0.65478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1507 | 3.3419 | 3.4467 | 2.4933 | 0.65478
| BOTWNNOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOULEVARD T1 / CHAPELFORD T1 / HAWLEYS LA T1 / WESTBROOK T1 / WINWICK QUAY T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.9326 | 1.9298 | 1.9265 | 1.9113 | 1.8699 | 1.8195 | 1.7696 | 1.716 | 1.6599 | 0 | 0 | 0 | 1.0267 | 0.68555 | 0 | 3.9672 | 3.6896 | 3.5118 | 3.4662 | 3.6826 | 3.625 | 3.5881 | 3.4869 | 3.3191 | 0 | 0 | 0 | 2.963 | 1.7906 | 0
| BOW ST T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 6.4873 | 6.3446 | 6.324 | 6.3681 | 6.3899 | 6.3734 | 6.3755 | 6.3097 | 6.3035 | 6.1838 | 6.0703 | 5.784 | 6.0799 | 5.727 | 4.5087 | 6.4873 | 6.3446 | 6.324 | 6.3681 | 6.3899 | 6.3734 | 6.3755 | 6.3097 | 6.3035 | 6.1838 | 6.0703 | 5.784 | 6.0799 | 5.727 | 4.5087
| BOWATER CONTAINERS T1 / ELLESMERE PORT LOCAL T1 / HH ROBERTSONS T1 / MOBIL OIL (E PORT) T1 / WHITBY T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 2.2392 | 2.3215 | 2.385 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0061 | 0 | 0 | 0 | 0 | 0 | 2.2392 | 2.3215 | 2.385 | 0 | 0 | 0 | 0 | 0 | 0 | 2.048 | 0
| BR STATION T1 / DUCHY RD T1 / ELECTRA WAY T1 / MIDLAND ROLLMAKERS T1A / NORTH WESTERN MILLS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH ALUMINIUM LATCHFORD T1 / GREENHALL WHITLEY T1 / LATCHFORD T1 / LATCHFORD T2 / THAMES BOARD MILL T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 1.7948 | 1.6606 | 1.6643 | 1.6668 | 1.6453 | 1.6186 | 1.5907 | 1.5602 | 1.5281 | 0 | 0 | 0 | 1.1804 | 1.0026 | 0 | 4.9397 | 4.5359 | 4.3511 | 4.3119 | 4.4606 | 4.4986 | 4.5224 | 4.4566 | 4.4987 | 0 | 0 | 0 | 4.5177 | 3.8403 | 0
| BRITISH OXYGEN T1 / WINDLEHURST T1 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0.36383 | 0.23672 | 0.19431 | 0.17518 | 0.21794 | 0.14198 | 0.054975 | 0.36314 | 0.33187 | 0.31329 | 0.25418 | 0.18242 | 0.13928 | 0 | 0 | 0.36383 | 0.23672 | 0.19431 | 0.17518 | 0.21794 | 0.14198 | 0.054975 | 0.36314 | 0.33187 | 0.31329 | 0.25418 | 0.18242 | 0.13928 | 0 | 0
| BRITISH PIPE ASSOCIATION T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH SIDAC T1 / SHERDLEY RD T1 / ST HELENS LINKWAY T1 / WATERY LA T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROADGREEN T1 / CROXTETH T1 / EAST PRESCOT RD (FINCH LA) T1 / KNOTTY ASH T1 / LEYFIELD RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMFIELD T1 / BROMFIELD T2 / PONTERWYL T1 / RHYD-Y-GOLEU T1 / SYNTHITE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 3.262 | 3.2592 | 3.2522 | 1.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3332 | 4.1311 | 3.9849 | 1.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROOK LA T1 / MANNINGS LA T1 / NEWTOWN CHESTER T1 / UPTON HEATH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROOK ST T1 / KINGSWAY TUNNEL T1 / NWWA SANDON DOCK T1 / NWWA SANDON DOCK T2 | 11 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRYN STANLEY T1 / DENBIGH T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUCKINGHAM ST T1 / EVERTON RD T1 / SUBURBAN RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUCKLEY T1 / BUCKLEY T2 / BUCKLEY CROSS T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0.87167 | 0.71326 | 0.60467 | 0.51844 | 0.60663 | 0.52475 | 0.4938 | 0.48752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87167 | 0.71326 | 0.60467 | 0.51844 | 0.60663 | 0.52475 | 0.4938 | 0.48752 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUILDWAS RD T1 / MORGAN REFRACTORIES T1 / NESTON MAIN T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 1.9597 | 1.8819 | 1.8609 | 1.8718 | 1.8635 | 1.8083 | 1.7631 | 1.6899 | 1.2585 | 1.0083 | 0.9987 | 1.1369 | 1.1855 | 0.36931 | 0 | 1.9597 | 1.8819 | 1.8609 | 1.8718 | 1.8635 | 1.8083 | 1.7631 | 1.6899 | 1.2585 | 1.0083 | 0.9987 | 1.1369 | 1.1855 | 0.36931 | 0
| BURLINGTON AVE T1 / FRESHFIELD T1 / MARSH BROWS T1 / SOUTHPORT RD T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 1.7919 | 1.5931 | 1.4964 | 1.3967 | 1.4517 | 1.283 | 1.1987 | 1.0634 | 0.88294 | 0.73314 | 0.64871 | 0.698 | 0.44948 | 0 | 0 | 1.7919 | 1.5931 | 1.4964 | 1.3967 | 1.4517 | 1.283 | 1.1987 | 1.0634 | 0.88294 | 0.73314 | 0.64871 | 0.698 | 0.44948 | 0 | 0
| BURMAH OIL T1 / CABOT CARBON T1 / VAN LEER NO 1 T1 | 7 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.71032 | 0.6477 | 0.60847 | 0.61026 | 0.68773 | 0.71048 | 0.70367 | 0.67018 | 0.66362 | 0.6681 | 0.66239 | 0.66854 | 0.70844 | 0.71927 | 0.67035 | 0.71032 | 0.6477 | 0.60847 | 0.61026 | 0.68773 | 0.71048 | 0.70367 | 0.67018 | 0.66362 | 0.6681 | 0.66239 | 0.66854 | 0.70844 | 0.71927 | 0.67035
| BUTLINS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 3.3324 | 3.1728 | 3.1067 | 3.1015 | 3.103 | 2.9717 | 2.4626 | 1.7812 | 1.2479 | 0.65539 | 0.24016 | 0 | 0 | 0 | 0 | 3.3324 | 3.1728 | 3.1067 | 3.1015 | 3.103 | 2.9717 | 2.4626 | 1.7812 | 1.2479 | 0.65539 | 0.24016 | 0 | 0 | 0 | 0
| BUTTINGTON CROSS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.0422 | 6.9839 | 6.9467 | 6.9474 | 7.0022 | 7.0007 | 6.9953 | 6.9513 | 6.9595 | 6.9711 | 0.39346 | 7.02 | 7.0633 | 7.0097 | 0 | 7.0422 | 6.9839 | 6.9467 | 6.9474 | 7.0022 | 7.0007 | 6.9953 | 6.9513 | 6.9595 | 6.9711 | 0.39346 | 7.02 | 7.0633 | 7.0097 | 0
| BXL BROMBOROUGH T1 / TULIP T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0.4497 | 0.37037 | 0.32558 | 0.34674 | 0.47195 | 0.50488 | 0 | 0 | 0 | 0 | 0 | 0.58376 | 0.72983 | 0 | 0 | 0.4497 | 0.37037 | 0.32558 | 0.34674 | 0.47195 | 0.50488 | 0 | 0 | 0 | 0 | 0 | 0.58376 | 0.72983 | 0 | 0
| CABLE ST T1 / GRADWELL ST T2 / OLDHAM PLACE T2 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CABLE ST T2 / CROWN COURTS T1 / GRADWELL ST T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CADBURYS KRONOSPAN T1 / CADBURYS KRONOSPAN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.5922 | 0.50747 | 0.46077 | 0.47998 | 0.57805 | 0.5965 | 0.60163 | 0.60123 | 0.58365 | 0.54884 | 0.39346 | 0.66093 | 0.77783 | 0.69228 | 0 | 0.5922 | 0.50747 | 0.46077 | 0.47998 | 0.57805 | 0.5965 | 0.60163 | 0.60123 | 0.58365 | 0.54884 | 0.39346 | 0.66093 | 0.77783 | 0.69228 | 0
| CADBURYS T1 / CADBURYS T2 / HOPFIELD RD T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAERGEILIOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.34479 | 0.31823 | 0.33227 | 0.32974 | 0.35925 | 0.35574 | 0.37793 | 0.41654 | 0.43853 | 0.49736 | 0.54971 | 0.76291 | 0 | 0 | 0 | 0.34479 | 0.31823 | 0.33227 | 0.32974 | 0.35925 | 0.35574 | 0.37793 | 0.41654 | 0.43853 | 0.49736 | 0.54971 | 0.76291 | 0 | 0 | 0
| CAERGWRLE T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0.62167 | 0.54577 | 0.53904 | 0.54297 | 0.57544 | 0.57457 | 0.56065 | 0.55534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62167 | 0.54577 | 0.53904 | 0.54297 | 0.57544 | 0.57457 | 0.56065 | 0.55534 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAERNARFON T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0.029175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047195 | 0.19676 | 0.52059 | 0.53436 | 0.19025 | 0.029175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047195 | 0.19676 | 0.52059 | 0.53436 | 0.19025
| CAERSWS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9557 | 6.4027 | 6.5112 | 6.5828 | 6.6261 | 6.611 | 6.5523 | 6.4747 | 6.4676 | 6.3094 | 0.39346 | 5.8651 | 6.089 | 6.0553 | 0 | 6.9557 | 6.4027 | 6.5112 | 6.5828 | 6.6261 | 6.611 | 6.5523 | 6.4747 | 6.4676 | 6.3094 | 0.39346 | 5.8651 | 6.089 | 6.0553 | 0
| CALDY T1 / HOYLAKE T1 / MEOLS T1 / WEST KIRBY SOUTH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 4.0572 | 3.8975 | 3.8034 | 3.7454 | 3.8556 | 3.7819 | 3.7966 | 3.7878 | 3.7727 | 3.7774 | 3.7843 | 3.9595 | 3.5746 | 1.8448 | 0 | 4.0572 | 3.8975 | 3.8034 | 3.7454 | 3.8556 | 3.7819 | 3.7966 | 3.7878 | 3.7727 | 3.7774 | 3.7843 | 3.9595 | 3.5746 | 1.8448 | 0
| CARBORUNDUM T1 / HOUGHTONS LA T1 / RAINFORD T1 / WINDLEHURST T2 | 11 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0.023834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CARLTON ST T1 / CARLTON ST T2 / CHALON WAY T2 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CARMEL T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.9274 | 2.3312 | 2.3199 | 2.348 | 2.3733 | 2.3794 | 2.378 | 2.1013 | 1.8079 | 1.362 | 0.91894 | 0 | 0 | 0 | 0 | 2.9274 | 2.3312 | 2.3199 | 2.348 | 2.3733 | 2.3794 | 2.378 | 2.1013 | 1.8079 | 1.362 | 0.91894 | 0 | 0 | 0 | 0
| CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 11 | CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | Yes | 2037 | 3.0747 | 2.1173 | 2.3995 | 2.4783 | 2.4632 | 2.4483 | 2.3925 | 2.3494 | 2.2949 | 2.2404 | 2.185 | 1.984 | 1.6691 | 1.443 | 0 | 4.5072 | 3.3761 | 3.4115 | 3.4087 | 3.6138 | 3.6887 | 3.6829 | 3.6546 | 3.5867 | 3.5619 | 3.5745 | 3.6512 | 3.345 | 2.1794 | 0
| CEFN MAWR T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0.044175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CEMAES BAY T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 3.2823 | 3.2691 | 3.279 | 3.3207 | 3.3193 | 3.3415 | 3.3482 | 3.3819 | 3.3832 | 3.3897 | 3.4033 | 1.6089 | 0 | 0 | 0 | 3.2823 | 3.2691 | 3.279 | 3.3207 | 3.3193 | 3.3415 | 3.3482 | 3.3819 | 3.3832 | 3.3897 | 3.4033 | 1.6089 | 0 | 0 | 0
| CEMMAES RD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.8189 | 2.6743 | 2.6656 | 2.7365 | 2.7172 | 2.7155 | 2.7107 | 2.6658 | 2.7018 | 2.6346 | 2.5074 | 2.4276 | 0 | 0 | 0 | 2.8189 | 2.6743 | 2.6656 | 2.7365 | 2.7172 | 2.7155 | 2.7107 | 2.6658 | 2.7018 | 2.6346 | 2.5074 | 2.4276 | 0 | 0 | 0
| CEREAL PARTNERS T1 / LEVER GEORGIA AVE T1 / POOL LA T1 / UML LEVER BROMBOROUGH T2 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHALON WAY T1 / TECHNOLOGY CAMPUS T1 / WOODVILLE ST T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 1.1613 | 1.0568 | 1.008 | 1.0319 | 1.1247 | 1.0368 | 0.99437 | 0.91586 | 0.86296 | 0 | 0 | 0.87118 | 0.85072 | 0.25233 | 0 | 1.1613 | 1.0568 | 1.008 | 1.0319 | 1.1247 | 1.0368 | 0.99437 | 0.91586 | 0.86296 | 0 | 0 | 0.87118 | 0.85072 | 0.25233 | 0
| CHESHIRE GREEN T1 / NWF T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0.52068 | 0.48052 | 0.44567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52068 | 0.48052 | 0.44567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESTER GATES T1 / UNILEVER DUNKIRK T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0.94335 | 0.97302 | 0.97364 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1153 | 0 | 0 | 0 | 0 | 0 | 0.94335 | 0.97302 | 0.97364 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1153 | 0
| CHESTER ST (WREXHAM) T1 / EAGLES MEADOW T1 / RHOSNESNI T1 / WHITEGATE T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 3.4147 | 3.2006 | 3.0748 | 3.027 | 3.1978 | 3.2218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4147 | 3.2006 | 3.0748 | 3.027 | 3.1978 | 3.2218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHILDWALL T1 / CHILDWALL FIVEWAYS T1 / LYNDENE RD T1 / MIDDLEMASS HEY T1 / NAYLORS RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHOWLEY T1 / CHOWLEY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 10.1997 | 10.1275 | 10.1042 | 10.124 | 10.155 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1997 | 10.1275 | 10.1042 | 10.124 | 10.155 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHURCH LA T1 / NANT HALL T1 / PRESTATYN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 2.4967 | 2.3361 | 2.2834 | 2.2162 | 2.3229 | 2.2937 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3761 | 1.5821 | 0 | 2.4967 | 2.3361 | 2.2834 | 2.2162 | 2.3229 | 2.2937 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3761 | 1.5821 | 0
| CHURCH LAWTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHURCH ST WINSFORD T1 / OVER T1 / WHARTON PK T1 / WOODFORD PK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 4.2572 | 3.9917 | 3.8375 | 3.7807 | 3.9535 | 3.8683 | 3.8541 | 3.8237 | 3.7388 | 3.6563 | 3.6707 | 3.8819 | 3.7071 | 2.346 | 0.47216 | 4.2572 | 3.9917 | 3.8375 | 3.7807 | 3.9535 | 3.8683 | 3.8541 | 3.8237 | 3.7388 | 3.6563 | 3.6707 | 3.8819 | 3.7071 | 2.346 | 0.47216
| CIVIC CENTRE T1 / CLAUGHTON AVE T1 / ELECTRICITY ST T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLEDFORD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLOCKFACE T1 / GEC ST HELENS T1 / HILLS MOSS T1 / NCB SUTTON MANOR T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLUBMOOR T1 / DUNLOPS WALTON T1 / WALTON T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLUBMOOR T2 / LISTER DV A T1 / SUBURBAN RD T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COEDPOETH T1 / COEDPOETH T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.3947 | 7.3235 | 7.3013 | 7.3201 | 7.4004 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3947 | 7.3235 | 7.3013 | 7.3201 | 7.4004 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COLWYN BAY T1 / COLWYN BAY T2 / RHOS-ON-SEA T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 1.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONEY GREEN T1 / OSWESTRY T2 / OSWESTRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 2.3897 | 1.996 | 1.8067 | 1.1454 | 0.81483 | 0.50042 | 0.19742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3897 | 1.996 | 1.8067 | 1.1454 | 0.81483 | 0.50042 | 0.19742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONIX T1 / CONIX T2 / MEDEVA T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONNAHS QUAY LOCAL T1 / CONNAHS QUAY LOCAL T2 / HAWARDEN T1 / KING GEORGE ST T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 3.3392 | 2.9464 | 2.6648 | 2.4174 | 2.4451 | 2.2551 | 2.0532 | 1.8293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3392 | 2.9464 | 2.6648 | 2.4174 | 2.4451 | 2.2551 | 2.0532 | 1.8293 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONWY T1 / DEGANWY T1 / LLANDUDNO JUNCTION T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CORWEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 7.0154 | 6.6496 | 6.6695 | 6.7204 | 6.7468 | 6.7164 | 6.7159 | 6.6009 | 6.6163 | 6.4526 | 6.3005 | 6.2658 | 0 | 0 | 0 | 7.0154 | 6.6496 | 6.6695 | 6.7204 | 6.7468 | 6.7164 | 6.7159 | 6.6009 | 6.6163 | 6.4526 | 6.3005 | 6.2658 | 0 | 0 | 0
| CREWE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRIGGION RADIO STATION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 2.9797 | 2.6552 | 2.6019 | 2.6269 | 2.6571 | 2.6017 | 2.5317 | 2.3588 | 2.3119 | 2.0794 | 0.39346 | 1.7601 | 1.9952 | 2.1114 | 0 | 2.9797 | 2.6552 | 2.6019 | 2.6269 | 2.6571 | 2.6017 | 2.5317 | 2.3588 | 2.3119 | 2.0794 | 0.39346 | 1.7601 | 1.9952 | 2.1114 | 0
| CROSSFIELDS T1 / CROSSFIELDS T2 / LEVERS CROSSFIELDS T3 / GATEWARTH SEWAGE T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 0.94469 | 0.80007 | 0.6977 | 0.65736 | 0.74804 | 0.70992 | 0.68446 | 0.6103 | 0.60621 | 0 | 0 | 0 | 0.73289 | 0.62095 | 0 | 0.94469 | 0.80007 | 0.6977 | 0.65736 | 0.74804 | 0.70992 | 0.68446 | 0.6103 | 0.60621 | 0 | 0 | 0 | 0.73289 | 0.62095 | 0
| CROWTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.22532 | 0.067209 | 0.037041 | 0.046685 | 0.077039 | 0.044017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22532 | 0.067209 | 0.037041 | 0.046685 | 0.077039 | 0.044017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CWM DYLI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.0724 | 1.9795 | 1.9502 | 1.9778 | 1.9942 | 1.973 | 1.963 | 1.9168 | 1.9441 | 1.8574 | 1.7686 | 1.509 | 0 | 0 | 0 | 2.0724 | 1.9795 | 1.9502 | 1.9778 | 1.9942 | 1.973 | 1.963 | 1.9168 | 1.9441 | 1.8574 | 1.7686 | 1.509 | 0 | 0 | 0
| DAILY POST & ECHO T1 / DAILY POST & ECHO T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DARESBURY NPL T1 / DARESBURY NPL T2 / DARESBURY PK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0.59032 | 0 | 0 | 0 | 0.002373 | 0.35191 | 0.36238 | 0.33915 | 0.16965 | 0.0027838 | 0 | 0 | 0.7503 | 0.7853 | 0.23926 | 0.59032 | 0 | 0 | 0 | 0.002373 | 0.35191 | 0.36238 | 0.33915 | 0.16965 | 0.0027838 | 0 | 0 | 0.7503 | 0.7853 | 0.23926
| DAVY WAY T1 / LLAY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE ALUMINIUM T1 / DUNLOP PLASTICS T1 / FIRESTONE T1 / TETRAPAK T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.9882 | 7.7675 | 7.5285 | 7.529 | 7.9551 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.14 | 7.7675 | 7.5285 | 7.529 | 7.9551 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE IND PK T1 / DEESIDE IND PK 6TH AVE T1 / RAF SEALAND T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | Yes | 2037 | 2.4077 | 2.2519 | 2.1633 | 2.1812 | 2.3947 | 2.5258 | 2.5835 | 2.6066 | 2.6122 | 2.6125 | 2.6805 | 2.9039 | 3.3102 | 3.4533 | 3.6499 | 2.4077 | 2.2519 | 2.1633 | 2.1812 | 2.3947 | 2.5258 | 2.5835 | 2.6066 | 2.6122 | 2.6125 | 2.6805 | 2.9039 | 3.3102 | 3.4533 | 3.6499
| DELAMORE ST T1 / KIRKDALE T1 / WALTON T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DESOTO RD T1 / MERSEY BRIDGE T1 / PITT ST T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 0.6139 | 0.55813 | 0.54902 | 0.62262 | 0.59019 | 0.51585 | 0.42678 | 0.37787 | 0.35198 | 0.33313 | 0.25431 | 0.20423 | 0.13805 | 0.057603 | 0 | 0.6139 | 0.55813 | 0.54902 | 0.62262 | 0.59019 | 0.51585 | 0.42678 | 0.37787 | 0.35198 | 0.33313 | 0.25431 | 0.20423 | 0.13805 | 0.057603
| DIBBINSDALE T1 / PLYMYARD T1 / WIBP HARDKNOTT RD T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 2.4447 | 2.3245 | 2.2562 | 2.2657 | 2.342 | 1.346 | 0 | 0 | 0 | 0 | 0 | 1.9298 | 1.6433 | 0 | 0 | 2.4447 | 2.3245 | 2.2562 | 2.2657 | 2.342 | 1.346 | 0 | 0 | 0 | 0 | 0 | 1.9298 | 1.6433 | 0 | 0
| DINGLE T1 / GRANBY T1 / ST JAMES T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DITTON T1 / GAVIN RD T1 / HOUGH GREEN T1 / RTZ T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 3.8826 | 3.7534 | 3.7727 | 3.847 | 3.6985 | 3.6018 | 3.4527 | 3.2796 | 3.1165 | 2.9995 | 2.8933 | 2.5488 | 1.3726 | 0 | 0 | 3.8826 | 3.7534 | 3.7727 | 3.847 | 3.6985 | 3.6018 | 3.4527 | 3.2796 | 3.1165 | 2.9995 | 2.8933 | 2.5488 | 1.3726 | 0
| DODDS LA T1 / HOLBORN HILL T1 / MAGHULL T1 / MAGHULL T2 / ROBBINS BRIDGE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 3.5594 | 3.5538 | 3.5464 | 3.4907 | 3.4175 | 3.3212 | 3.2184 | 3.1102 | 2.9956 | 2.8657 | 2.734 | 2.3231 | 1.5881 | 0.58184 | 0 | 6.2994 | 5.678 | 5.5531 | 5.156 | 5.1599 | 5.0124 | 4.802 | 4.6404 | 4.4066 | 4.1716 | 4.0633 | 4.1521 | 3.5916 | 0.58184 | 0
| DOLGARROG T1 / DOLGARROG T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DOLGELLAU T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 8.9984 | 8.9815 | 9.0113 | 9.0881 | 9.1118 | 9.1528 | 9.2254 | 9.3203 | 9.4139 | 9.5185 | 9.5926 | 7.0761 | 0 | 0 | 0 | 8.9984 | 8.9815 | 9.0113 | 9.0881 | 9.1118 | 9.1528 | 9.2254 | 9.3203 | 9.4139 | 9.5185 | 9.5926 | 7.0761 | 0 | 0 | 0
| DUCKINGTON T1 / DUCKINGTON T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DUDDON T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DYFFRYN ARDUDWY T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.8374 | 9.6809 | 9.6624 | 9.6782 | 9.6913 | 9.6793 | 9.7148 | 9.6415 | 9.6926 | 9.5631 | 9.4093 | 7.0761 | 0 | 0 | 0 | 9.8374 | 9.6809 | 9.6624 | 9.6782 | 9.6913 | 9.6793 | 9.7148 | 9.6415 | 9.6926 | 9.5631 | 9.4093 | 7.0761 | 0 | 0 | 0
| DYSERTH RD T1 / FFORDD LAS T1 / FFORDD LAS T2 / WESTBOURNE AVE T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 5.3492 | 4.8007 | 4.5881 | 4.3198 | 4.3482 | 4.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4638 | 3.2061 | 0 | 5.3492 | 4.8007 | 4.5881 | 4.3198 | 4.3482 | 4.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4638 | 3.2061 | 0
| EDEN VALE T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 7.0847 | 7.0197 | 7.0056 | 7.006 | 7.0285 | 6.9489 | 6.8773 | 6.8114 | 6.7363 | 6.6699 | 6.629 | 6.5687 | 6.5356 | 6.2428 | 5.6053 | 7.0847 | 7.0197 | 7.0056 | 7.006 | 7.0285 | 6.9489 | 6.8773 | 6.8114 | 6.7363 | 6.6699 | 6.629 | 6.5687 | 6.5356 | 6.2428 | 5.6053
| EDERN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.07741 | 0.065159 | 0.092334 | 0.166 | 0.18456 | 0.24787 | 0.3193 | 0.3844 | 0.46676 | 0.55088 | 0.64384 | 0.91378 | 0 | 0 | 0 | 0.07741 | 0.065159 | 0.092334 | 0.166 | 0.18456 | 0.24787 | 0.3193 | 0.3844 | 0.46676 | 0.55088 | 0.64384 | 0.91378 | 0 | 0 | 0
| EDGE HILL T1 / LIVERPOOL UNIVERSITY T1 / LIVERPOOL UNIVERSITY T2 / LIVERPOOL UNIVERSITY T3 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EDGE LA (TAPLEY PLACE) T1 / LISTER DV B T3 / MILL LA (WAVERTREE) T1 / PLESSEY (EDGE LA) T1 / STONEYCROFT T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EGA ELECTRIC T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 6.4292 | 6.3685 | 6.3511 | 6.3541 | 6.3808 | 6.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3046 | 4.1762 | 0 | 6.4292 | 6.3685 | 6.3511 | 6.3541 | 6.3808 | 6.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3046 | 4.1762 | 0
| EGERTON T1 / ROCK FERRY T1 / SHELL TRANMERE T1 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EGREMONT T1 / LISCARD T1 / POULTON T1 / STONE MANGANESE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELLESMERE T1 / MMB ELLESMERE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0 | 0 | 0 | 0.021324 | 0.036575 | 0.039416 | 0.02282 | 0.036514 | 0.035395 | 0.039747 | 0.070809 | 0.1985 | 0.39788 | 0.33494 | 0.14198 | 0 | 0 | 0 | 0.021324 | 0.036575 | 0.039416 | 0.02282 | 0.036514 | 0.035395 | 0.039747 | 0.070809 | 0.1985 | 0.39788 | 0.33494 | 0.14198
| ENGINEER PK T1 / PILKINGTONS QUEENSFERRY T1 / QUEENSFERRY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ESTUARY COMMERCE PK T1 / LEEWARD DR T1 / LEEWARD DR T2 / SPEKE HALL RD T1 / SPEKE SKY PK T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EVERTON BROW T1 / GARDNERS ROW T1 / SHEIL PK T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EXPRESS FOODS T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FAIRBOURNE T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 9.2548 | 9.0969 | 9.085 | 9.1365 | 9.1354 | 9.1385 | 9.1429 | 9.0559 | 9.1225 | 8.9927 | 8.9005 | 8.8275 | 9.3071 | 9.3639 | 8.7421 | 9.2548 | 9.0969 | 9.085 | 9.1365 | 9.1354 | 9.1385 | 9.1429 | 9.0559 | 9.1225 | 8.9927 | 8.9005 | 8.8275 | 9.3071 | 9.3639 | 8.7421
| FAZAKERLEY HOSPITAL T1 / JACOBS T1 / JACOBS T2 / SEEDS LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 3.3394 | 3.019 | 2.8511 | 2.7333 | 2.7876 | 2.7508 | 2.7344 | 2.6631 | 2.6983 | 2.8126 | 2.9223 | 1.9396 | 0 | 0 | 0 | 3.3394 | 3.019 | 2.8511 | 2.7333 | 2.7876 | 2.7508 | 2.7344 | 2.6631 | 2.6983 | 2.8126 | 2.9223 | 1.9396 | 0 | 0 | 0
| FERODO T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.6672 | 6.6519 | 6.6401 | 6.6545 | 6.6828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 6.6672 | 6.6519 | 6.6401 | 6.6545 | 6.6828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| FLINT T1 / FLINT T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FODENS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORD T1 / OXTON T1 / PRENTON LOCAL T1 / SINGLETON AVE T2 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORDEN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 3.4447 | 4.6578 | 4.6156 | 4.6265 | 4.6452 | 4.604 | 4.5647 | 4.4303 | 4.4067 | 4.2367 | 0.39346 | 3.4522 | 3.6538 | 3.4101 | 0 | 3.4447 | 4.6578 | 4.6156 | 4.6265 | 4.6452 | 4.604 | 4.5647 | 4.4303 | 4.4067 | 4.2367 | 0.39346 | 3.4522 | 3.6538 | 3.4101 | 0
| FOUR CROSSES T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.5874 | 1.471 | 1.0657 | 0.84464 | 0.78207 | 0.74302 | 0.30817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5874 | 1.471 | 1.0657 | 0.84464 | 0.78207 | 0.74302 | 0.30817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRODSHAM LOCAL T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.79532 | 0.74507 | 0.73996 | 0.75635 | 0.82324 | 0.80821 | 0.78857 | 0.79301 | 0.78487 | 0.75386 | 0.77913 | 0.9697 | 1.026 | 0.52491 | 0 | 0.79532 | 0.74507 | 0.73996 | 0.75635 | 0.82324 | 0.80821 | 0.78857 | 0.79301 | 0.78487 | 0.75386 | 0.77913 | 0.9697 | 1.026 | 0.52491 | 0
| GADBROOK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 6.9272 | 6.8662 | 6.8464 | 6.8582 | 6.8921 | 6.8554 | 6.8318 | 6.7764 | 6.7336 | 6.6785 | 6.6712 | 6.6502 | 6.6354 | 6.3053 | 5.7417 | 6.9272 | 6.8662 | 6.8464 | 6.8582 | 6.8921 | 6.8554 | 6.8318 | 6.7764 | 6.7336 | 6.6785 | 6.6712 | 6.6502 | 6.6354 | 6.3053 | 5.7417
| GAERWEN VIEW T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 9.7898 | 9.7754 | 9.7693 | 9.7875 | 9.7972 | 9.803 | 9.7882 | 9.7965 | 9.8005 | 9.8145 | 9.8041 | 1.6089 | 0 | 0 | 0 | 9.7898 | 9.7754 | 9.7693 | 9.7875 | 9.7972 | 9.803 | 9.7882 | 9.7965 | 9.8005 | 9.8145 | 9.8041 | 1.6089 | 0 | 0 | 0
| GIGG LA THELWALL T1 / HILLCLIFFE T1 / STOCKTON HEATH T1 / STRETTON IND EST T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 4.8247 | 4.5089 | 4.3402 | 4.1616 | 4.2613 | 4.1044 | 3.9405 | 3.7374 | 3.5027 | 0 | 0 | 0 | 2.2131 | 0.19483 | 0 | 4.8247 | 4.5089 | 4.3402 | 4.1616 | 4.2613 | 4.1044 | 3.9405 | 3.7374 | 3.5027 | 0 | 0 | 0 | 2.2131 | 0.19483 | 0
| GILBROOK DOCK T1 / HILL RD T1 / MOBIL OIL (WALLASEY) T1 | 7 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLAN-YR-AFON T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.35791 | 0.24324 | 0.21154 | 0.22821 | 0.25149 | 0.22299 | 0.20807 | 0.10623 | 0.087779 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35791 | 0.24324 | 0.21154 | 0.22821 | 0.25149 | 0.22299 | 0.20807 | 0.10623 | 0.087779 | 0 | 0 | 0 | 0 | 0 | 0
| GRAIG FAWR T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 8.0917 | 8.0741 | 8.1048 | 8.1676 | 8.1762 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4721 | 4.1762 | 0 | 8.0917 | 8.0741 | 8.1048 | 8.1676 | 8.1762 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4721 | 4.1762 | 0
| GRAVEL T1 / WCB PLASTICS T1 / WHARTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 1.0897 | 1.0176 | 0.96269 | 0.96129 | 1.0604 | 1.0726 | 1.0388 | 0.98554 | 0.95939 | 0.90338 | 0.89597 | 0.86584 | 0.9042 | 0.86679 | 0.79006 | 1.0897 | 1.0176 | 0.96269 | 0.96129 | 1.0604 | 1.0726 | 1.0388 | 0.98554 | 0.95939 | 0.90338 | 0.89597 | 0.86584 | 0.9042 | 0.86679 | 0.79006
| GREASBY T1 / SAUGHALL MASSIE T1 / UPTON T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 2.7557 | 2.5742 | 2.4829 | 2.4175 | 2.4653 | 2.3664 | 2.2825 | 2.2289 | 2.131 | 2.0413 | 2 | 2.0765 | 1.8694 | 0.71739 | 0 | 2.7557 | 2.5742 | 2.4829 | 2.4175 | 2.4653 | 2.3664 | 2.2825 | 2.2289 | 2.131 | 2.0413 | 2 | 2.0765 | 1.8694 | 0.71739 | 0
| GREAT SANKEY T1 / PENKETH T1 / WIDNES RD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 2.1397 | 2.0207 | 1.9757 | 1.9716 | 1.8933 | 1.7691 | 1.6536 | 1.5713 | 1.443 | 0 | 0 | 0 | 0.89563 | 0 | 0 | 2.1397 | 2.0207 | 1.9757 | 1.9716 | 1.8933 | 1.7691 | 1.6536 | 1.5713 | 1.443 | 0 | 0 | 0 | 0.89563 | 0 | 0
| GREAT SUTTON T1 / LITTLE SUTTON T1 / STRAWBERRY ROUNDABOUT T1 / SUTTON HALL WWB T1 / WHITBY MAIN T2 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 3.2193 | 3.147 | 3.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2979 | 0 | 0 | 0 | 0 | 0 | 5.5536 | 5.5188 | 5.4302 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7432 | 0
| GREENFIELD T1 / GREENFIELD T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GROSVENOR ST T1 / LINENHALL ST T1 / NORTHGATE TERRACE T1 / STATION VIEW T1 / TOMULAR PLACE T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GWERSYLLT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 9.8597 | 9.8013 | 9.7828 | 9.844 | 9.838 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8597 | 9.8013 | 9.7828 | 9.844 | 9.838 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HALTON RD T1 / MURDISHAW T1 / PERCIVAL LA T4 / RUNCORN CENTRAL T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARLECH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 6.8699 | 6.7992 | 6.8261 | 6.8587 | 6.8576 | 6.9029 | 6.9355 | 6.9902 | 7.0346 | 7.0864 | 7.1441 | 7.0761 | 0 | 0 | 0 | 6.8699 | 6.7992 | 6.8261 | 6.8587 | 6.8576 | 6.9029 | 6.9355 | 6.9902 | 7.0346 | 7.0864 | 7.1441 | 7.0761 | 0 | 0 | 0
| HARRINGTON ST T1 / PARADISE ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARRINGTON ST T2 / HIGHFIELD ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARRINGTON ST T3 / LIME ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARTFORD T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0.022192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HASKAYNE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HATHERTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HERONS WAY T1 / LACHE T1 / MBNA T1 / SMFS KINGSMEADOW T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HIGHFIELD ST T2 / LIME ST T2 / OLD HAYMARKET T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLMES CHAPEL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLT LA (WARRINGTON RD) T1 / PRESCOT T1 / RAINHILL LOCAL T1 / WHISTON HOSP T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 4.1885 | 4.024 | 3.8528 | 3.7998 | 3.6843 | 3.667 | 3.6312 | 3.4846 | 3.3373 | 3.2508 | 3.1643 | 2.9071 | 1.7881 | 0 | 0 | 4.1885 | 4.024 | 3.8528 | 3.7998 | 3.6843 | 3.667 | 3.6312 | 3.4846 | 3.3373 | 3.2508 | 3.1643 | 2.9071 | 1.7881 | 0
| HOLWAY RD T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 7.5997 | 7.5481 | 6.5162 | 1.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5997 | 7.5481 | 6.5162 | 1.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLYHEAD T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.024788 | 0 | 0 | 0.0066954 | 0.026471 | 0.027929 | 0.049903 | 0.090137 | 0.10225 | 0.14632 | 0.16962 | 0.30484 | 0 | 0 | 0 | 0.024788 | 0 | 0 | 0.0066954 | 0.026471 | 0.027929 | 0.049903 | 0.090137 | 0.10225 | 0.14632 | 0.16962 | 0.30484 | 0 | 0 | 0
| HOLYWELL T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.18917 | 0.1749 | 0.20048 | 0.23649 | 0.20621 | 0.19758 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.057652 | 0 | 0.18917 | 0.1749 | 0.20048 | 0.23649 | 0.20621 | 0.19758 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.057652 | 0
| HOOTON MAIN T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 9.1707 | 9.171 | 9.2082 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5216 | 0 | 0 | 0 | 0 | 0 | 9.1707 | 9.171 | 9.2082 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5216 | 0
| HUNTS CROSS T1 / KENTON RD T1 / WOODEND AVE T1 / WOOLTON T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HUYTON HEY RD T1 / WILSON RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IFTON T1 / IFTON T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.5172 | 7.4638 | 7.4368 | 7.4793 | 7.4877 | 7.4664 | 7.4594 | 7.457 | 7.4358 | 7.3966 | 0.39346 | 7.4821 | 7.5066 | 7.1059 | 0 | 7.5172 | 7.4638 | 7.4368 | 7.4793 | 7.4877 | 7.4664 | 7.4594 | 7.457 | 7.4358 | 7.3966 | 0.39346 | 7.4821 | 7.5066 | 7.1059 | 0
| ILFORDS T1 / KNUTSFORD T1 / MOBBERLEY T1 / RADBROKE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 1.5195 | 1.3668 | 1.2724 | 1.2869 | 1.4705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 1.5195 | 1.3668 | 1.2724 | 1.2869 | 1.4705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| IVY ST (SOUTHPORT) T1 / KENSINGTON RD T1 / MARKET ST T1 / SOUTHPORT T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 3.1744 | 2.9498 | 2.8187 | 2.8243 | 3.0478 | 3.1369 | 3.1956 | 3.2178 | 3.2997 | 3.3188 | 3.3892 | 3.6828 | 4.077 | 4.0001 | 3.8422 | 3.1744 | 2.9498 | 2.8187 | 2.8243 | 3.0478 | 3.1369 | 3.1956 | 3.2178 | 3.2997 | 3.3188 | 3.3892 | 3.6828 | 4.077 | 4.0001 | 3.8422
| IVY ST T1 / LLYSFAEN RD T1 / OLD MILL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| JOHNSTOWN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.6097 | 7.5365 | 7.5163 | 7.5811 | 7.6996 | 7.7275 | 7.7876 | 7.7888 | 7.795 | 7.8067 | 0.39346 | 8.0277 | 8.3181 | 8.3668 | 0 | 7.6097 | 7.5365 | 7.5163 | 7.5811 | 7.6996 | 7.7275 | 7.7876 | 7.7888 | 7.795 | 7.8067 | 0.39346 | 8.0277 | 8.3181 | 8.3668 | 0
| KELCO T1 / NEWS INTERNATIONAL T1 / NEWS INTERNATIONAL T2 / PALCO T1 / SOUTHDENE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KINGSLAND 33 T1 / SAFEWAY T1 / WOOLSTON T1 / WOOLSTON T2 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 3.5772 | 3.1606 | 2.9677 | 2.7851 | 2.7428 | 2.6428 | 2.6095 | 2.5382 | 2.5317 | 0 | 0 | 0 | 2.4707 | 1.4549 | 0 | 3.5772 | 3.1606 | 2.9677 | 2.7851 | 2.7428 | 2.6428 | 2.6095 | 2.5382 | 2.5317 | 0 | 0 | 0 | 2.4707 | 1.4549 | 0
| KINNERTON T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 9.9817 | 9.9773 | 9.9849 | 10.0434 | 10.0425 | 10.0602 | 10.0727 | 4.5395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9817 | 9.9773 | 9.9849 | 10.0434 | 10.0425 | 10.0602 | 10.0727 | 4.5395 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KIRKBY CENTRAL T1 / NORTHWOOD T1 / TOWER HILL (BANK LA) T1 / WESTVALE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KNOWSLEY T1 / MARLED HEY T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KNUTSFORD T2 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 1.3618 | 1.2855 | 1.2664 | 1.2877 | 1.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 1.3618 | 1.2855 | 1.2664 | 1.2877 | 1.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| LCWW HUNTINGTON T1 / LCWW HUNTINGTON T2 | 7 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEA GREEN T1 / PILKINGTONS HO T1 / RAVENHEAD RETAIL PK T1 / SOMERFIELD DISTRIBUTION T1 | 11 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEGACY LOCAL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 4.1997 | 4.1223 | 4.1035 | 4.084 | 4.075 | 4.0314 | 4.0083 | 3.9952 | 3.9621 | 3.9275 | 0.39346 | 3.9259 | 3.9126 | 3.7878 | 0 | 4.1997 | 4.1223 | 4.1035 | 4.084 | 4.075 | 4.0314 | 4.0083 | 3.9952 | 3.9621 | 3.9275 | 0.39346 | 3.9259 | 3.9126 | 3.7878 | 0
| LEIGHTON HOSP T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LIVERPOOL RD 33 T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 4.5272 | 4.4641 | 4.4335 | 4.4476 | 4.5045 | 4.5102 | 4.5237 | 4.5218 | 4.5178 | 4.5151 | 4.5022 | 4.5719 | 4.57 | 4.4212 | 4.0454 | 4.5272 | 4.4641 | 4.4335 | 4.4476 | 4.5045 | 4.5102 | 4.5237 | 4.5218 | 4.5178 | 4.5151 | 4.5022 | 4.5719 | 4.57 | 4.4212 | 4.0454
| LLAINGOCH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.14729 | 0.095048 | 0.10822 | 0.1286 | 0.16988 | 0.1725 | 0.20346 | 0.24227 | 0.25155 | 0.28624 | 0.31341 | 0.44837 | 0 | 0 | 0 | 0.14729 | 0.095048 | 0.10822 | 0.1286 | 0.16988 | 0.1725 | 0.20346 | 0.24227 | 0.25155 | 0.28624 | 0.31341 | 0.44837 | 0 | 0 | 0
| LLANARMON T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 9.5567 | 9.4068 | 9.3886 | 9.4053 | 9.3818 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5425 | 4.1762 | 0 | 9.5567 | 9.4068 | 9.3886 | 9.4053 | 9.3818 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5425 | 4.1762 | 0
| LLANBEDROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.3024 | 8.8143 | 8.4605 | 8.1544 | 7.5454 | 6.3259 | 5.7978 | 5.1262 | 4.5875 | 3.9637 | 3.5647 | 2.8514 | 0 | 0 | 0 | 9.3024 | 8.8143 | 8.4605 | 8.1544 | 7.5454 | 6.3259 | 5.7978 | 5.1262 | 4.5875 | 3.9637 | 3.5647 | 2.8514 | 0 | 0 | 0
| LLANBERIS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 6.3392 | 6.1851 | 6.2053 | 6.2328 | 6.2854 | 6.2888 | 6.315 | 6.3309 | 6.337 | 6.378 | 6.3987 | 6.4686 | 6.491 | 6.3679 | 6.2643 | 6.3392 | 6.1851 | 6.2053 | 6.2328 | 6.2854 | 6.2888 | 6.315 | 6.3309 | 6.337 | 6.378 | 6.3987 | 6.4686 | 6.491 | 6.3679 | 6.2643
| LLANDDEUSANT T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDDU QUARRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 1.3397 | 1.2626 | 1.2136 | 1.2049 | 1.2468 | 1.2276 | 1.1955 | 1.1517 | 1.1182 | 0.67405 | 0.39346 | 0.056783 | 0.10661 | 0 | 0 | 1.3397 | 1.2626 | 1.2136 | 1.2049 | 1.2468 | 1.2276 | 1.1955 | 1.1517 | 1.1182 | 0.67405 | 0.39346 | 0.056783 | 0.10661 | 0 | 0
| LLANDEGFAN T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 6.4183 | 6.3939 | 6.399 | 6.3965 | 6.3839 | 6.3459 | 6.3356 | 6.3017 | 6.2894 | 6.2528 | 6.2276 | 1.6089 | 0 | 0 | 0 | 6.4183 | 6.3939 | 6.399 | 6.3965 | 6.3839 | 6.3459 | 6.3356 | 6.3017 | 6.2894 | 6.2528 | 6.2276 | 1.6089 | 0 | 0 | 0
| LLANDRINIO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 3.1122 | 2.9672 | 2.971 | 3.0125 | 2.9955 | 2.9554 | 2.9073 | 2.7966 | 2.7445 | 2.5994 | 0.39346 | 2.1103 | 2.3709 | 2.3395 | 0 | 3.1122 | 2.9672 | 2.971 | 3.0125 | 2.9955 | 2.9554 | 2.9073 | 2.7966 | 2.7445 | 2.5994 | 0.39346 | 2.1103 | 2.3709 | 2.3395 | 0
| LLANDUDNO T1 / LLANDUDNO T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 1.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDYFRYDOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.4398 | 7.2929 | 7.2814 | 7.3172 | 7.2997 | 7.2799 | 7.2602 | 6.9163 | 6.6143 | 6.083 | 5.3241 | 1.6089 | 0 | 0 | 0 | 7.4398 | 7.2929 | 7.2814 | 7.3172 | 7.2997 | 7.2799 | 7.2602 | 6.9163 | 6.6143 | 6.083 | 5.3241 | 1.6089 | 0 | 0 | 0
| LLANDYRNOG T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFAELOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 4.0298 | 4.0128 | 4.0169 | 4.0289 | 4.0676 | 4.0792 | 4.0859 | 4.0871 | 4.085 | 4.0924 | 4.1045 | 1.6089 | 0 | 0 | 0 | 4.0298 | 4.0128 | 4.0169 | 4.0289 | 4.0676 | 4.0792 | 4.0859 | 4.0871 | 4.085 | 4.0924 | 4.1045 | 1.6089 | 0 | 0 | 0
| LLANFAIR CAEREINION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 4.5122 | 4.4335 | 4.4001 | 4.416 | 4.4228 | 4.3933 | 4.3784 | 4.3535 | 4.3475 | 4.3486 | 0.39346 | 4.1888 | 4.4378 | 4.3617 | 0 | 4.5122 | 4.4335 | 4.4001 | 4.416 | 4.4228 | 4.3933 | 4.3784 | 4.3535 | 4.3475 | 4.3486 | 0.39346 | 4.1888 | 4.4378 | 4.3617 | 0
| LLANFAIR PG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.8798 | 7.8127 | 7.8125 | 7.8026 | 7.8462 | 7.8807 | 7.8883 | 7.9082 | 7.9028 | 7.9211 | 7.9315 | 1.6089 | 0 | 0 | 0 | 7.8798 | 7.8127 | 7.8125 | 7.8026 | 7.8462 | 7.8807 | 7.8883 | 7.9082 | 7.9028 | 7.9211 | 7.9315 | 1.6089 | 0 | 0 | 0
| LLANFAIRFECHAN T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 6.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFROTHEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.2174 | 9.1007 | 9.1172 | 9.1506 | 9.1503 | 9.1679 | 9.1922 | 9.233 | 9.26 | 9.2932 | 9.3635 | 7.0761 | 0 | 0 | 0 | 9.2174 | 9.1007 | 9.1172 | 9.1506 | 9.1503 | 9.1679 | 9.1922 | 9.233 | 9.26 | 9.2932 | 9.3635 | 7.0761 | 0 | 0 | 0
| LLANFWROG T1 / RUTHIN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFYLLIN T1 / LLANFYLLIN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANGAFFO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.5698 | 7.4306 | 7.4395 | 7.4598 | 7.4616 | 7.4438 | 7.3888 | 7.3022 | 7.2566 | 7.1175 | 6.9284 | 1.6089 | 0 | 0 | 0 | 7.5698 | 7.4306 | 7.4395 | 7.4598 | 7.4616 | 7.4438 | 7.3888 | 7.3022 | 7.2566 | 7.1175 | 6.9284 | 1.6089 | 0 | 0 | 0
| LLANGEFNI IND EST T1 / LLANGEFNI IND EST T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 1.4523 | 1.2821 | 1.2067 | 1.2111 | 1.3061 | 1.3442 | 1.3238 | 1.2366 | 1.2437 | 0.59343 | 0.086354 | 0 | 0 | 0 | 0 | 1.4523 | 1.2821 | 1.2067 | 1.2111 | 1.3061 | 1.3442 | 1.3238 | 1.2366 | 1.2437 | 0.59343 | 0.086354 | 0 | 0 | 0 | 0
| LLANGEFNI T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.2298 | 10.2003 | 10.1803 | 10.1845 | 10.2113 | 10.2131 | 10.2251 | 10.2165 | 10.2146 | 10.2264 | 10.2237 | 1.6089 | 0 | 0 | 0 | 10.2298 | 10.2003 | 10.1803 | 10.1845 | 10.2113 | 10.2131 | 10.2251 | 10.2165 | 10.2146 | 10.2264 | 10.2237 | 1.6089 | 0 | 0 | 0
| LLANGOLLEN T1 / LLANGOLLEN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.2397 | 0.19594 | 0.20857 | 0.23185 | 0.24871 | 0.21532 | 0.19882 | 0.19564 | 0.18235 | 0.17825 | 0.18587 | 0.2549 | 0.1257 | 0 | 0 | 0.2397 | 0.19594 | 0.20857 | 0.23185 | 0.24871 | 0.21532 | 0.19882 | 0.19564 | 0.18235 | 0.17825 | 0.18587 | 0.2549 | 0.1257 | 0 | 0
| LLANIDLOES T1 / LLANIDLOES T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANILAR T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 1.9173 | 1.78 | 1.774 | 1.8123 | 1.8231 | 1.7939 | 1.7581 | 1.6619 | 1.6463 | 1.5133 | 1.3861 | 1.1138 | 1.3969 | 1.5055 | 0.77857 | 1.9173 | 1.78 | 1.774 | 1.8123 | 1.8231 | 1.7939 | 1.7581 | 1.6619 | 1.6463 | 1.5133 | 1.3861 | 1.1138 | 1.3969 | 1.5055 | 0.77857
| LLANRWST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 7.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANSANNAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 9.8467 | 9.5797 | 9.5789 | 9.642 | 9.6308 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6652 | 4.1762 | 0 | 9.8467 | 9.5797 | 9.5789 | 9.642 | 9.6308 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6652 | 4.1762 | 0
| LLANSILIN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 8.4982 | 8.3424 | 8.3242 | 8.3626 | 8.3766 | 8.3526 | 8.3047 | 8.222 | 8.2263 | 8.0831 | 0.39346 | 7.684 | 7.9709 | 7.8532 | 0 | 8.4982 | 8.3424 | 8.3242 | 8.3626 | 8.3766 | 8.3526 | 8.3047 | 8.222 | 8.2263 | 8.0831 | 0.39346 | 7.684 | 7.9709 | 7.8532 | 0
| LLYNCLYS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9777 | 6.9647 | 6.9539 | 7.0162 | 7.0516 | 7.0687 | 7.0807 | 7.0965 | 7.0684 | 7.0174 | 0.39346 | 7.1396 | 7.4034 | 7.5673 | 0 | 6.9777 | 6.9647 | 6.9539 | 7.0162 | 7.0516 | 7.0687 | 7.0807 | 7.0965 | 7.0684 | 7.0174 | 0.39346 | 7.1396 | 7.4034 | 7.5673 | 0
| LORD ST T1 / MARSHSIDE T1 / MULLARDS BALMORAL DV T1 / SOUTHPORT T2 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 3.8394 | 3.1483 | 3.2259 | 3.0635 | 3.0349 | 2.8298 | 2.7193 | 2.6776 | 2.5631 | 2.4247 | 2.44 | 2.9237 | 2.9293 | 0.34817 | 0 | 3.8394 | 3.1483 | 3.2259 | 3.0635 | 3.0349 | 2.8298 | 2.7193 | 2.6776 | 2.5631 | 2.4247 | 2.44 | 2.9237 | 2.9293 | 0.34817 | 0
| LOSTOCK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LOSTOCK TRIANGLE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 9.1922 | 9.1737 | 9.172 | 9.1945 | 9.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 9.1922 | 9.1737 | 9.172 | 9.1945 | 9.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| LOWER BEBINGTON T1 / NEW FERRY T1 / SPITAL T1 / UNILEVER RESEARCH T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LUGSDALE T1 / PILK SULLIVAN T1 / PILK SULLIVAN T2 / USAC T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 2.047 | 1.9602 | 1.9691 | 2.1208 | 2.1165 | 2.0731 | 1.9822 | 1.9205 | 1.9335 | 1.9275 | 1.8786 | 1.8419 | 1.7372 | 1.5047 | 0 | 2.047 | 1.9602 | 1.9691 | 2.1208 | 2.1165 | 2.0731 | 1.9822 | 1.9205 | 1.9335 | 1.9275 | 1.8786 | 1.8419 | 1.7372 | 1.5047
| LYMM T1 / WHITELEGGS LA T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 1.2072 | 1.0729 | 1.0438 | 1.0033 | 1.0333 | 0.92973 | 0.856 | 0.79731 | 0.68734 | 0 | 0 | 0 | 0.61601 | 0 | 0 | 1.2072 | 1.0729 | 1.0438 | 1.0033 | 1.0333 | 0.92973 | 0.856 | 0.79731 | 0.68734 | 0 | 0 | 0 | 0.61601 | 0 | 0
| MACHYNLLETH T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 3.2828 | 3.2835 | 3.3041 | 3.3584 | 3.3778 | 3.4117 | 3.4547 | 3.5086 | 3.5373 | 3.5969 | 3.6663 | 3.8595 | 4.0266 | 4.0338 | 3.9556 | 3.2828 | 3.2835 | 3.3041 | 3.3584 | 3.3778 | 3.4117 | 3.4547 | 3.5086 | 3.5373 | 3.5969 | 3.6663 | 3.8595 | 4.0266 | 4.0338 | 3.9556
| MACHYNLLETH T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 4.3976 | 4.1279 | 4.0359 | 3.9937 | 3.9457 | 3.8782 | 3.8503 | 3.7783 | 3.6391 | 3.516 | 3.3759 | 3.0913 | 3.3174 | 3.1754 | 2.5185 | 4.3976 | 4.1279 | 4.0359 | 3.9937 | 3.9457 | 3.8782 | 3.8503 | 3.7783 | 3.6391 | 3.516 | 3.3759 | 3.0913 | 3.3174 | 3.1754 | 2.5185
| MAELOR CREAMERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 9.3797 | 9.1901 | 9.1249 | 9.1212 | 9.1486 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3797 | 9.1901 | 9.1249 | 9.1212 | 9.1486 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MAENTWROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.1949 | 9.0305 | 9.0158 | 9.0495 | 9.0354 | 9.0123 | 9.0021 | 8.9352 | 8.9497 | 8.8288 | 8.716 | 7.0761 | 0 | 0 | 0 | 9.1949 | 9.0305 | 9.0158 | 9.0495 | 9.0354 | 9.0123 | 9.0021 | 8.9352 | 8.9497 | 8.8288 | 8.716 | 7.0761 | 0 | 0 | 0
| MAES-Y-CLAWDD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 5.9347 | 5.8603 | 5.8215 | 5.8168 | 5.8839 | 5.9019 | 5.9088 | 5.8841 | 5.9527 | 5.9842 | 0.39346 | 6.2504 | 6.5613 | 6.5982 | 0 | 5.9347 | 5.8603 | 5.8215 | 5.8168 | 5.8839 | 5.9019 | 5.9088 | 5.8841 | 5.9527 | 5.9842 | 0.39346 | 6.2504 | 6.5613 | 6.5982 | 0
| MANOD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.7729 | 2.6464 | 2.6304 | 2.6638 | 2.6599 | 2.6656 | 2.6463 | 2.5686 | 2.6003 | 2.4851 | 2.3725 | 2.049 | 0 | 0 | 0 | 2.7729 | 2.6464 | 2.6304 | 2.6638 | 2.6599 | 2.6656 | 2.6463 | 2.5686 | 2.6003 | 2.4851 | 2.3725 | 2.049 | 0 | 0 | 0
| MANOR PK T1 / NORTON CHAINS T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 2.0378 | 1.9916 | 2.0006 | 2.0748 | 2.1323 | 2.1741 | 2.2594 | 2.293 | 2.3983 | 2.2924 | 2.4071 | 3.0509 | 3.628 | 3.8064 | 3.8121 | 2.0378 | 1.9916 | 2.0006 | 2.0748 | 2.1323 | 2.1741 | 2.2594 | 2.293 | 2.3983 | 2.2924 | 2.4071 | 3.0509 | 3.628 | 3.8064 | 3.8121
| MDHB EGERTON DOCK T1 / MDHB EGERTON DOCK T2 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MERE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.9497 | 6.9552 | 6.9894 | 7.0313 | 6.9976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 6.9497 | 6.9552 | 6.9894 | 7.0313 | 6.9976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| MERES EDGE T1 / MERES EDGE T2 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 10.4053 | 10.3717 | 6.9437 | 10.4535 | 10.45 | 10.4593 | 10.4684 | 10.4905 | 10.4984 | 10.4873 | 10.5271 | 10.6501 | 10.7346 | 10.5023 | 10.0707 | 10.4053 | 10.3717 | 6.9437 | 10.4535 | 10.45 | 10.4593 | 10.4684 | 10.4905 | 10.4984 | 10.4873 | 10.5271 | 10.6501 | 10.7346 | 10.5023 | 10.0707
| MIDDLEWICH T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MIDPOINT POCHIN WAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 8.9122 | 8.891 | 8.8782 | 8.8791 | 8.9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 8.9122 | 8.891 | 8.8782 | 8.8791 | 8.9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| MILFORD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MINFFORDD T1 / PARC BRYN CEGIN T1 / PARC BRYN CEGIN T2 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 1.0717 | 1.0388 | 1.0216 | 1.0437 | 1.0775 | 1.0695 | 1.0702 | 1.0667 | 1.0582 | 1.0534 | 1.0585 | 1.1124 | 1.1489 | 0.98444 | 0.81577 | 1.0717 | 1.0388 | 1.0216 | 1.0437 | 1.0775 | 1.0695 | 1.0702 | 1.0667 | 1.0582 | 1.0534 | 1.0585 | 1.1124 | 1.1489 | 0.98444 | 0.81577
| MOCHDRE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9472 | 6.7962 | 6.7423 | 6.7456 | 6.8115 | 6.8136 | 6.7822 | 6.6676 | 6.6492 | 6.5077 | 0.39346 | 5.7387 | 5.9787 | 5.8665 | 0 | 6.9472 | 6.7962 | 6.7423 | 6.7456 | 6.8115 | 6.8136 | 6.7822 | 6.6676 | 6.6492 | 6.5077 | 0.39346 | 5.7387 | 5.9787 | 5.8665 | 0
| MONA T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 5.2973 | 3.7857 | 4.7492 | 5.1183 | 5.1664 | 5.1228 | 5.0619 | 4.9139 | 4.8934 | 4.666 | 4.4445 | 1.6089 | 0 | 0 | 0 | 5.2973 | 3.7857 | 4.7492 | 5.1183 | 5.1664 | 5.1228 | 5.0619 | 4.9139 | 4.8934 | 4.666 | 4.4445 | 1.6089 | 0 | 0 | 0
| MONSANTO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MORDA T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 8.8697 | 4.8549 | 5.2152 | 5.7672 | 6.352 | 7.0221 | 7.0314 | 6.9867 | 6.6917 | 6.3584 | 0.39346 | 5.9672 | 7.5962 | 8.1808 | 0 | 8.8697 | 4.8549 | 5.2152 | 5.7672 | 6.352 | 7.0221 | 7.0314 | 6.9867 | 6.6917 | 6.3584 | 0.39346 | 5.9672 | 7.5962 | 8.1808 | 0
| MORGANITE CERAMICS T1 / PLYMYARD T2 / VAUXHALL NORTH RD T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MORRISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 7.3172 | 7.2569 | 7.2204 | 7.2319 | 7.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 7.3172 | 7.2569 | 7.2204 | 7.2319 | 7.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| NANTWICH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NANT-Y-GAMAR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 0.35917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NEVILL ST T1 / OCEAN PLAZA T1 / YORK RD T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 1.9769 | 1.8427 | 1.7626 | 1.792 | 1.9798 | 2.0133 | 2.0492 | 2.0442 | 2.04 | 2.0267 | 2.0399 | 2.1526 | 2.2587 | 2.0528 | 1.7225 | 1.9769 | 1.8427 | 1.7626 | 1.792 | 1.9798 | 2.0133 | 2.0492 | 2.0442 | 2.04 | 2.0267 | 2.0399 | 2.1526 | 2.2587 | 2.0528 | 1.7225
| NEW BRIGHTON T1 / SEAVIEW RD T2 / WALLASEY T1 / WALLASEY VILLAGE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NEWHALL T1 / NEWHALL T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NORTH WALES PAPER T1 / NORTH WALES PAPER T2 / WOODFIELD AVE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 3.2592 | 3.0933 | 2.9885 | 1.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2592 | 3.0933 | 2.9885 | 1.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NORTH WEST WATER CAMPUS T1 / NORTH WEST WATER CAMPUS T2 / OMEGA T1 / OMEGA T2 / ORION BOULEVARD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OPTICAL FIBRES T1 / SHOTWICK T1 / WALBRO T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | Yes | 2037 | 1.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ORB CL T1 / STONEBRIDGE LA T1 / STONEBRIDGE LA T2 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 0.16693 | 0.043825 | 0 | 0 | 0.13475 | 0.13243 | 0.12391 | 0.097476 | 0.050653 | 0 | 0 | 0.073 | 0 | 0 | 0 | 0.16693 | 0.043825 | 0 | 0 | 0.13475 | 0.13243 | 0.12391 | 0.097476 | 0.050653 | 0 | 0 | 0.073 | 0 | 0 | 0
| ORFORD T1 / PADGATE T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.1822 | 1.1844 | 1.2692 | 1.2994 | 1.1936 | 1.0599 | 0.9858 | 0.937 | 0.91033 | 0 | 0 | 0 | 1.1403 | 0.25219 | 0 | 1.1822 | 1.1844 | 1.2692 | 1.2994 | 1.1936 | 1.0599 | 0.9858 | 0.937 | 0.91033 | 0 | 0 | 0 | 1.1403 | 0.25219 | 0
| OTIS ELEVATOR T1 / ST IVEL FOODS T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OVERTON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.4847 | 0.38406 | 0.38842 | 0.27145 | 0.24157 | 0.24389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4847 | 0.38406 | 0.38842 | 0.27145 | 0.24157 | 0.24389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PANDY T1 / PANDY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 1.0672 | 0.85208 | 0.76735 | 0.65984 | 0.64091 | 0.56998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0672 | 0.85208 | 0.76735 | 0.65984 | 0.64091 | 0.56998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PARC CYBI T1 / PARC CYBI T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.57979 | 0.55318 | 0.54558 | 0.56773 | 0.61107 | 0.63662 | 0.66359 | 0.66794 | 0.68887 | 0.68913 | 0.69779 | 0.80761 | 0 | 0 | 0 | 0.57979 | 0.55318 | 0.54558 | 0.56773 | 0.61107 | 0.63662 | 0.66359 | 0.66794 | 0.68887 | 0.68913 | 0.69779 | 0.80761 | 0 | 0 | 0
| PARC MENAI T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 7.0417 | 7.0236 | 7.0216 | 7.0351 | 7.0388 | 7.0358 | 7.0403 | 7.0127 | 7.006 | 7.001 | 6.9798 | 7.0208 | 7.0704 | 7.0903 | 6.9659 | 7.0417 | 7.0236 | 7.0216 | 7.0351 | 7.0388 | 7.0358 | 7.0403 | 7.0127 | 7.006 | 7.001 | 6.9798 | 7.0208 | 7.0704 | 7.0903 | 6.9659
| PEBLIC MILLS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PENMAENMAWR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 9.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PENTRAETH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.4523 | 10.4197 | 10.4322 | 10.4285 | 10.461 | 10.4575 | 10.4608 | 10.4754 | 10.4532 | 10.4275 | 10.4505 | 1.6089 | 0 | 0 | 0 | 10.4523 | 10.4197 | 10.4322 | 10.4285 | 10.461 | 10.4575 | 10.4608 | 10.4754 | 10.4532 | 10.4275 | 10.4505 | 1.6089 | 0 | 0 | 0
| PEN-Y-GROES T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 3.2812 | 2.8813 | 3.0114 | 3.0775 | 3.0936 | 3.0956 | 3.1101 | 3.1427 | 3.1657 | 3.1997 | 3.208 | 3.3394 | 3.417 | 3.2911 | 3.0062 | 3.2812 | 2.8813 | 3.0114 | 3.0775 | 3.0936 | 3.0956 | 3.1101 | 3.1427 | 3.1657 | 3.1997 | 3.208 | 3.3394 | 3.417 | 3.2911 | 3.0062
| PILKINGTONS T1 / PILKINGTONS T2 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.53917 | 0.35499 | 0.30089 | 0.3052 | 0.31319 | 0.28455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53917 | 0.35499 | 0.30089 | 0.3052 | 0.31319 | 0.28455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| POINT OF AYR COLLIERY T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.45167 | 0.42017 | 0.39687 | 0.41926 | 0.49334 | 0.50681 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83898 | 0.82831 | 0 | 0.45167 | 0.42017 | 0.39687 | 0.41926 | 0.49334 | 0.50681 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83898 | 0.82831 | 0
| PORTHMADOG T1 / PORTHMADOG T2 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.86741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PREES T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 9.8447 | 9.6245 | 9.5186 | 9.4179 | 9.3578 | 9.2809 | 9.2191 | 9.1479 | 9.1555 | 8.9588 | 8.6627 | 8.2612 | 8.2017 | 7.7013 | 6.6478 | 9.8447 | 9.6245 | 9.5186 | 9.4179 | 9.3578 | 9.2809 | 9.2191 | 9.1479 | 9.1555 | 8.9588 | 8.6627 | 8.2612 | 8.2017 | 7.7013 | 6.6478
| PRIMROSE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.6447 | 6.6229 | 6.603 | 6.6128 | 6.6424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 6.6447 | 6.6229 | 6.603 | 6.6128 | 6.6424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| PWLLHELI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 7.6949 | 7.6378 | 7.6141 | 7.6249 | 7.673 | 7.6767 | 7.6939 | 7.7209 | 7.7366 | 7.7864 | 7.8195 | 7.0761 | 0 | 0 | 0 | 7.6949 | 7.6378 | 7.6141 | 7.6249 | 7.673 | 7.6767 | 7.6939 | 7.7209 | 7.7366 | 7.7864 | 7.8195 | 7.0761 | 0 | 0 | 0
| RADWAY GREEN T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RAVEN SQUARE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05005 | 0 | 0
| REFORM ST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 10.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHM FOODS LTD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHOSLAN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.9369 | 9.914 | 9.9262 | 9.9989 | 10.0139 | 10.0574 | 10.1349 | 10.2103 | 10.269 | 10.3326 | 10.3943 | 7.0761 | 0 | 0 | 0 | 9.9369 | 9.914 | 9.9262 | 9.9989 | 10.0139 | 10.0574 | 10.1349 | 10.2103 | 10.269 | 10.3326 | 10.3943 | 7.0761 | 0 | 0 | 0
| RHUDDLAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 6.7042 | 6.6028 | 6.5929 | 6.562 | 6.5449 | 6.5222 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5164 | 4.1762 | 0 | 6.7042 | 6.6028 | 6.5929 | 6.562 | 6.5449 | 6.5222 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5164 | 4.1762 | 0
| RHYDLYDAN T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 1.5673 | 1.5684 | 1.5807 | 1.6062 | 1.6294 | 1.6281 | 1.6227 | 1.6016 | 1.6023 | 1.618 | 1.6146 | 1.7155 | 1.7424 | 1.7127 | 1.635 | 1.5673 | 1.5684 | 1.5807 | 1.6062 | 1.6294 | 1.6281 | 1.6227 | 1.6016 | 1.6023 | 1.618 | 1.6146 | 1.7155 | 1.7424 | 1.7127 | 1.635
| RHYD-Y-FOEL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RINGWAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.5372 | 6.2938 | 6.3107 | 6.3509 | 6.4103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0 | 6.5372 | 6.2938 | 6.3107 | 6.3509 | 6.4103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| RIVALS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 3.6424 | 3.5903 | 3.5937 | 3.6256 | 4.8334 | 4.8388 | 4.8435 | 4.8356 | 4.8475 | 4.8396 | 4.738 | 4.2221 | 0 | 0 | 0 | 3.6424 | 3.5903 | 3.5937 | 3.6256 | 4.8334 | 4.8388 | 4.8435 | 4.8356 | 4.8475 | 4.8396 | 4.738 | 4.2221 | 0 | 0 | 0
| ROLLS ROYCE T1 / ROLLS ROYCE T2 / ROLLS ROYCE T3 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROSSETT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 8.8397 | 8.7796 | 8.8465 | 8.9667 | 9.0115 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8397 | 8.7796 | 8.8465 | 8.9667 | 9.0115 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROYAL INSURANCE (NEW QUAY) T1 / ROYAL INSURANCE (NEW QUAY) T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RUABON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALTNEY T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SANDBACH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHAWBURY T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMALLWOOD T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SNOWHILL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ST ASAPH BUSINESS PK T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 10.2741 | 10.1908 | 10.2754 | 10.3933 | 10.472 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0039 | 4.1762 | 0 | 10.2741 | 10.1908 | 10.2754 | 10.3933 | 10.472 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0039 | 4.1762 | 0
| ST HELENS RD T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0.21917 | 0.17396 | 0.14972 | 0.17015 | 0.22693 | 0.22333 | 0.22506 | 0.25365 | 0.25127 | 0.27578 | 0.28978 | 0.37718 | 0.43175 | 0.32252 | 0.17953 | 0.21917 | 0.17396 | 0.14972 | 0.17015 | 0.22693 | 0.22333 | 0.22506 | 0.25365 | 0.25127 | 0.27578 | 0.28978 | 0.37718 | 0.43175 | 0.32252 | 0.17953
| STAPELEY T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TACO PLASTICS T1 / TACO PLASTICS T2 / UNITED PERIPHERALS T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 1.8552 | 1.7302 | 1.6446 | 1.7002 | 1.8893 | 1.9564 | 1.9905 | 1.9547 | 1.9616 | 2.0449 | 2.0986 | 2.1723 | 2.2227 | 2.0283 | 1.7451 | 1.8552 | 1.7302 | 1.6446 | 1.7002 | 1.8893 | 1.9564 | 1.9905 | 1.9547 | 1.9616 | 2.0449 | 2.0986 | 2.1723 | 2.2227 | 2.0283 | 1.7451
| TARPORLEY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.0672 | 7.0122 | 7.0004 | 7.0261 | 7.0415 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0672 | 7.0122 | 7.0004 | 7.0261 | 7.0415 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TARVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRYWERYN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 4.6274 | 4.1988 | 4.2819 | 4.3754 | 4.4355 | 4.3863 | 4.3688 | 4.2558 | 4.2526 | 4.1066 | 3.9309 | 3.6878 | 0 | 0 | 0 | 4.6274 | 4.1988 | 4.2819 | 4.3754 | 4.4355 | 4.3863 | 4.3688 | 4.2558 | 4.2526 | 4.1066 | 3.9309 | 3.6878 | 0 | 0 | 0
| TWYFORDS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TYWYN T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 7.1823 | 7.1689 | 7.1912 | 7.2708 | 7.2659 | 7.2789 | 7.3322 | 7.3861 | 7.4673 | 7.5523 | 7.6211 | 7.9315 | 8.0366 | 7.7431 | 7.3367 | 7.1823 | 7.1689 | 7.1912 | 7.2708 | 7.2659 | 7.2789 | 7.3322 | 7.3861 | 7.4673 | 7.5523 | 7.6211 | 7.9315 | 8.0366 | 7.7431 | 7.3367
| WAENFAWR T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 9.1077 | 8.6385 | 8.6621 | 8.6928 | 8.6866 | 8.7006 | 8.7238 | 8.7458 | 8.772 | 8.8106 | 8.8173 | 8.8895 | 9.3159 | 9.1638 | 8.4313 | 9.1077 | 8.6385 | 8.6621 | 8.6928 | 8.6866 | 8.7006 | 8.7238 | 8.7458 | 8.772 | 8.8106 | 8.8173 | 8.8895 | 9.3159 | 9.1638 | 8.4313
| WELSHPOOL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEM EAST T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEM T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WERVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEST FELTON T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 7.7672 | 7.648 | 7.5696 | 7.583 | 7.6396 | 7.5751 | 7.5185 | 7.3448 | 7.3286 | 7.073 | 6.5534 | 5.9925 | 6.1009 | 5.8732 | 4.8828 | 7.7672 | 7.648 | 7.5696 | 7.583 | 7.6396 | 7.5751 | 7.5185 | 7.3448 | 7.3286 | 7.073 | 6.5534 | 5.9925 | 6.1009 | 5.8732 | 4.8828
| WESTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WHEELOCK T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WHITCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 5.7972 | 5.7099 | 5.6808 | 5.6682 | 5.6871 | 5.6333 | 5.5892 | 5.5515 | 5.5129 | 5.4749 | 5.4717 | 5.5427 | 5.4972 | 5.141 | 4.6796 | 5.7972 | 5.7099 | 5.6808 | 5.6682 | 5.6871 | 5.6333 | 5.5892 | 5.5515 | 5.5129 | 5.4749 | 5.4717 | 5.5427 | 5.4972 | 5.141 | 4.6796
| WIMPEYS PANT QUARRY T1 / WIMPEYS PANT QUARRY T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0.68417 | 0.5234 | 0.45451 | 0.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68417 | 0.5234 | 0.45451 | 0.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WINCHAM T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 6.5697 | 6.5513 | 6.5423 | 6.5515 | 6.5932 | 6.5467 | 6.5068 | 6.45 | 6.4097 | 6.3528 | 6.3088 | 6.2593 | 6.2047 | 6.1249 | 6.0491 | 6.5697 | 6.5513 | 6.5423 | 6.5515 | 6.5932 | 6.5467 | 6.5068 | 6.45 | 6.4097 | 6.3528 | 6.3088 | 6.2593 | 6.2047 | 6.1249 | 6.0491
| WISTASTON HALL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WRENBURY FRITH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| YOCKINGS GATE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| YSBYTY GLAN CLWYD T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 5.7067 | 5.6575 | 5.6258 | 5.6351 | 5.6816 | 5.6849 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8927 | 4.1762 | 0 | 5.7067 | 5.6575 | 5.6258 | 5.6351 | 5.6816 | 5.6849 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8927 | 4.1762 | 0
Grid Groups | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 33 | SWANSEA NORTH | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 6.8433 | 5.2852 | 4.8432 | 3.3408 | 3.4327 | 1.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4943 | 0 | 0 | 34.2166 | 26.4262 | 24.2158 | 16.7041 | 17.1633 | 8.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5191 | 0 | 0
| FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 33 | TRAWSFYNYDD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 33 | CELLARHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 33 | KIRKBY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 33 | KIRKBY | Yes | 2037 | 19.5203 | 18.6013 | 17.5258 | 16.506 | 15.5009 | 14.391 | 13.2531 | 12.9579 | 12.6241 | 12.3483 | 12.0487 | 11.0464 | 9.8326 | 8.5393 | 7.3522 | 66.4062 | 64.3916 | 62.2273 | 60.8256 | 60.7258 | 59.7134 | 58.6063 | 58.2645 | 57.368 | 56.9059 | 56.6168 | 55.2321 | 49.1628 | 42.6966 | 36.761
| AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 33 | KIRKBY | Yes | 2037 | 3.6894 | 3.65 | 3.5163 | 3.3803 | 3.279 | 3.0603 | 2.8189 | 2.5042 | 2.1404 | 1.8288 | 1.4872 | 0.38793 | 0 | 0 | 0 | 18.4472 | 18.2498 | 17.5816 | 16.9016 | 16.3951 | 15.3016 | 14.0945 | 12.521 | 10.702 | 9.1442 | 7.4362 | 1.9396 | 0 | 0 | 0
| CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 5.341 | 3.8046 | 3.0466 | 2.7902 | 4.3632 | 3.7509 | 2.9321 | 0.90789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.7049 | 19.023 | 15.2329 | 13.9512 | 21.8159 | 18.7547 | 14.6605 | 4.5395 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 33 | KIRKBY | Yes | 2037 | 13.3525 | 12.6274 | 11.8744 | 11.3463 | 11.2992 | 10.7416 | 10.4153 | 9.438 | 8.6434 | 7.3248 | 6.7347 | 5.9739 | 6.15 | 4.8448 | 1.3563 | 63.9395 | 61.8637 | 59.3721 | 56.7317 | 56.4962 | 53.7082 | 52.0765 | 47.19 | 43.2169 | 36.6239 | 33.6736 | 29.8694 | 30.7501 | 24.2239 | 6.7813
| AMLWCH GT1 / CAERGEILIOG GT1 | 33 | WYLFA | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 10.8137 | 10.6731 | 11.1932 | 11.929 | 13.1006 | 9.2119 | 7.9128 | 7.35 | 6.687 | 6.4386 | 6.7092 | 8.5564 | 8.1598 | 6.8784 | 3.7522 | 54.0684 | 53.3654 | 55.9658 | 59.6452 | 65.5028 | 46.0593 | 39.5642 | 36.7499 | 33.4349 | 32.1931 | 33.5462 | 42.7818 | 40.799 | 34.3919 | 18.7612
| BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 33 | RAINHILL | Yes | 2037 | 0 | 8.8327 | 4.499 | 4.6758 | 6.0001 | 5.2438 | 7.0392 | 8.5304 | 10.253 | 9.0335 | 8.8329 | 10.7363 | 15.6597 | 16.9919 | 14.6387 | 0 | 32.1811 | 22.4952 | 23.379 | 29.9495 | 26.2192 | 30.0099 | 30.7943 | 31.3555 | 29.7079 | 29.0773 | 29.9966 | 34.257 | 31.6903 | 24.4343
| HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 33 | BIRKENHEAD | Yes | 2037 | 5.9072 | 5.9058 | 5.8966 | 5.8232 | 5.7482 | 5.5822 | 5.4195 | 5.2975 | 5.2667 | 5.2875 | 5.3355 | 6.3267 | 5.4098 | 4.6389 | 3.7978 | 29.5361 | 29.529 | 29.4831 | 29.1162 | 28.7409 | 27.9111 | 27.0975 | 26.4873 | 26.3337 | 26.4377 | 26.6774 | 31.6333 | 27.0489 | 23.1946 | 18.9888
| BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 33 | LEGACY | Yes | 2037 | 24.1408 | 20.039 | 15.5863 | 11.0325 | 6.5383 | 1.3703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1055 | 100.195 | 77.9313 | 55.1625 | 32.6915 | 6.8516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 33 | CAPENHURST | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 33 | FRODSHAM - INCE | Yes | 2037 | 10.4504 | 10.3461 | 10.1853 | 9.6973 | 7.6227 | 7.333 | 6.6158 | 6.4485 | 5.9469 | 5.6631 | 5.852 | 6.9121 | 7.2733 | 5.0695 | 2.8799 | 48.5922 | 47.2999 | 44.1136 | 38.3849 | 35.517 | 33.8219 | 31.0509 | 31.1206 | 29.7347 | 28.3153 | 29.2601 | 34.5603 | 36.3666 | 25.3477 | 14.3997
| BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BANGOR GT2 / CAERNARFON GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 14.1254 | 9.4542 | 8.1003 | 6.096 | 6.7703 | 4.7187 | 3.5346 | 2.9307 | 1.7803 | 0.65687 | 0 | 0 | 0 | 0 | 0 | 14.1254 | 9.4542 | 8.1003 | 6.096 | 6.7703 | 4.7187 | 3.5346 | 2.9307 | 1.7803 | 0.65687 | 0 | 0 | 0 | 0 | 0
| DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 4.2875 | 3.6913 | 4.3451 | 5.7794 | 9.5945 | 10.186 | 8.9357 | 6.8105 | 4.0047 | 0 | 0 | 0 | 6.5487 | 7.3923 | 0 | 9.9197 | 8.1335 | 7.8895 | 7.7355 | 11.8708 | 11.1757 | 9.2261 | 13.2854 | 10.4134 | 0 | 0 | 0 | 15.5989 | 15.6744 | 0
| OSWESTRY GT5 / WHITCHURCH GT1 | 33 | LEGACY | Yes | 2037 | 39.3925 | 38.7318 | 37.6408 | 36.3091 | 34.7672 | 32.7233 | 31.0059 | 30.0322 | 28.6025 | 27.3672 | 26.0822 | 22.7224 | 18.9511 | 14.7356 | 11.2547 | 126.9658 | 124.8184 | 121.5117 | 117.3248 | 112.9757 | 105.9823 | 98.722 | 93.9671 | 87.3608 | 81.6365 | 75.5056 | 56.8891 | 44.0261 | 26.4612 | 11.5404
| GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PRENTON GRID GT1 / ROCK FERRY GT1 | 33 | BIRKENHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 33 | FRODSHAM - INCE | Yes | 2037 | 5.2937 | 2.1011 | 1.3887 | 3.1802 | 6.113 | 7.6439 | 8.9163 | 9.7384 | 10.9534 | 10.8263 | 10.8092 | 10.7193 | 12.7689 | 13.5944 | 13.8066 | 21.1425 | 10.5057 | 6.9437 | 10.0204 | 13.2546 | 14.8228 | 15.9977 | 16.5423 | 16.9852 | 16.4917 | 16.3669 | 14.6947 | 17.2662 | 16.7224 | 14.388
| BOOTLE GT1 / LITHERLAND GT1A | 33 | KIRKBY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 33 | CAPENHURST | Yes | 2037 | 0 | 0 | 0 | 0 | 2.4807 | 7.2605 | 4.2192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1057 | 12.0969 | 7.3361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 33 | LEGACY | Yes | 2037 | 18.1776 | 12.2041 | 5.4124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1776 | 12.2041 | 5.4124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SANKEY BRIDGES GT3 / WARRINGTON GT5 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 33 | RAINHILL | Yes | 2037 | 7.7806 | 5.6759 | 3.7837 | 1.8035 | 0.61207 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7403 | 9.0771 | 5.2557 | 1.1639 | 7.7806 | 5.6759 | 3.7837 | 1.8035 | 0.61207 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7403 | 9.0771 | 5.2557 | 1.1639
| BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 2.9733 | 2.0481 | 1.3032 | 0.38997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8663 | 10.2407 | 6.5162 | 1.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMBOROUGH GT3 / ROCK FERRY GT2 | 33 | BIRKENHEAD | Yes | 2037 | 7.6334 | 5.7804 | 3.3738 | 1.9206 | 1.4221 | 0.20183 | 0 | 0 | 0 | 0 | 0 | 3.3058 | 0.32866 | 0 | 0 | 7.6334 | 5.7804 | 3.3738 | 1.9206 | 1.5139 | 0.20183 | 0 | 0 | 0 | 0 | 0 | 4.6284 | 1.6433 | 0 | 0
| WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 33 | BIRKENHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 10.8137 | 8.1512 | 8.1363 | 10.1474 | 13.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083564 | 0 | 0 | 54.0684 | 40.7559 | 40.6817 | 50.7369 | 65.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41782 | 0 | 0
| HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 4.5582 | 11.7978 | 9.7513 | 8.3171 | 9.0685 | 6.858 | 5.2138 | 4.7356 | 4.4346 | 3.5815 | 2.5469 | 0 | 0 | 0 | 0 | 4.5582 | 11.7978 | 9.7513 | 8.3171 | 9.0685 | 6.858 | 5.2138 | 4.7356 | 4.4346 | 3.5815 | 2.5469 | 0 | 0 | 0 | 0

## High Scenario (Gen)
Generation Headroom (MW)
Return to Contents |  |  |  | Subject to upstream constraints beyond our network boundary (Yes/No) (See section 7.3 of the methodology statement) | Expected upsteam capacity release date (provided by National Grid Electricity Transmission) | Synchronous | [14 empty] | Fully Converted
| Group Name | Voltage (kV) | Grid / GSP Group |  |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2035 | 2040 | 2045 | 2050
Primary Groups | ABERDYFI T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 7.0173 | 7.0664 | 7.0406 | 6.9655 | 6.8895 | 6.878 | 6.8375 | 6.8549 | 6.9252 | 6.9528 | 7.0155 | 7.1164 | 6.8802 | 6.1334 | 5.4278 | 7.0173 | 7.0664 | 7.0406 | 6.9655 | 6.8895 | 6.878 | 6.8375 | 6.8549 | 6.9252 | 6.9528 | 7.0155 | 7.1164 | 6.8802 | 6.1334 | 5.4278
| ABERGELE T1 / PENSARN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 1.6617 | 1.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6617 | 1.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ABERSOCH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ABERYSTWYTH T1 / NORTH RD T1 / PARC-Y-LLYN T1 / PARC-Y-LLYN T2 / U C WALES T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 5.1952 | 5.1928 | 5.1699 | 5.1208 | 5.067 | 5.0084 | 4.9426 | 4.8792 | 4.8154 | 4.745 | 4.6673 | 4.4385 | 4.0219 | 3.5709 | 2.3533 | 5.4223 | 5.613 | 5.5986 | 5.531 | 5.3369 | 5.3756 | 5.4324 | 5.5216 | 5.6264 | 5.9134 | 6.3299 | 8.143 | 8.669 | 5.981 | 2.3533
| ACER AVE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACORNFIELD RD T1 / DICKINSONS T1 / HAMMOND RD T1 / KODAK T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIGBURTH VALE T1 / IVY AVE T1 / MATHER AVE T1 / MOSSLEY HILL T1 / WAVERTREE T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AINSDALE T1 / PINFOLD LA T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 0.49443 | 0.58621 | 0.49439 | 0.21688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49443 | 0.58621 | 0.49439 | 0.21688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AINTREE LOCAL T1 / OLD ROAN T1 / WANGO LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 2.3344 | 2.4189 | 2.3857 | 2.1704 | 1.8288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3344 | 2.4189 | 2.3857 | 2.1704 | 1.8288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIRBUS T1 / BROUGHTON RETAIL PARK T1 / MIXALLOY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 1.3332 | 0.5249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3332 | 0.5249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AIRPORT T1 / ALDERWOOD AVE (CROYDE RD) T1 / HAREFIELD RD T1 / METAL BOX (SPEKE) T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALBERT DOCK T1 / KINGS DOCK T1 / KINGS DOCK T2 / WAPPING T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALLERTON T1 / ECP WEST-BANKS RD T1 / GARSTON T1 / WEAVER IND EST T1 / YEW TREE RD T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALMATEX T1 / ST HELENS WWTW T1 / WATERY LA T2 / ex DELTA METALS T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0.24685 | 0.24685 | 0.24245 | 0.19001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2343 | 1.2343 | 1.2123 | 0.95004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALMONDS TURN T1 / ATLANTIC COMPLEX T1 / GIRO T1 / MIDLAND BANK T1 / NETHERTON T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 1.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ALPOCO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AMLWCH T1 / AMLWCH T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ANDERTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| APPLETON T1 / HORNSBRIDGE T1 / LUGSDALE T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 3.0096 | 2.8879 | 2.4708 | 0 | 0 | 0 | 1.1494 | 0.94999 | 0.79701 | 0.64011 | 0.38954 | 0 | 0 | 0 | 0 | 3.0096 | 2.8879 | 2.4708 | 0 | 0 | 0 | 1.1494 | 0.94999 | 0.79701 | 0.64011 | 0.38954 | 0 | 0 | 0
| ARROWE PK HOSP T1 / CHAMPION PLUGS T1 / CHAMPION PLUGS T2 / WOODCHURCH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32425 | 0 | 0
| ARUNDEL T1 / GROVE PK T1 / WAVERTREE VALE T1 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASH RD T1 / KELLOGGS (WREXHAM) T1 / KELLOGGS (WREXHAM) T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 1.7222 | 0.049509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7222 | 0.049509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASSOCIATED LEAD T1 / GREAT BOUGHTON T1 / PIPERS ASH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASTMOOR IND EST T1 / MACKAMAX T1 / MERSEY RD T1 / PICOW FARM RD T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ATHOL ST T1 / CHISENHALE ST T1 / SANDHILLS LA T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AUDLEM T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BALA T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.2554 | 9.2004 | 9.1851 | 9.1496 | 9.1768 | 9.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2554 | 9.2004 | 9.1851 | 9.1496 | 9.1768 | 9.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BANASTRE RD T1 / DOVER RD T1 / GRANTHAM CL T1 | 7 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 2.1094 | 2.2205 | 2.0944 | 1.7425 | 1.3043 | 0.96725 | 0.66933 | 0.40044 | 0.075981 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1094 | 2.2205 | 2.0944 | 1.7425 | 1.3043 | 0.96725 | 0.66933 | 0.40044 | 0.075981 | 0 | 0 | 0 | 0 | 0 | 0
| BANGOR HOSP T1 / BANGOR UNIVERSITY T1 / EITHINOG T1 / HIRAEL T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BARBAULD ST T1 / HORROCKS LA T1 / WARRINGTON CENTRAL T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.6497 | 1.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6497 | 1.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BARMOUTH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.8134 | 9.4766 | 9.49 | 9.5269 | 9.5723 | 9.6268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8134 | 9.4766 | 9.49 | 9.5269 | 9.5723 | 9.6268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BARNSTON T1 / GAYTON T1 / IRBY T1 / THINGWALL T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 4.6697 | 4.782 | 4.5805 | 4.0368 | 3.6395 | 3.279 | 2.9185 | 2.5514 | 2.2272 | 1.7733 | 1.1976 | 0.4061 | 0 | 0 | 0 | 4.6697 | 4.782 | 4.5805 | 4.0368 | 3.6395 | 3.279 | 2.9185 | 2.5514 | 2.2272 | 1.7733 | 1.1976 | 0.4061 | 0 | 0 | 0
| BASCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BASS CHARRINGTON T1 / BASS CHARRINGTON T2 / CLIFTON T1 / YKK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 2.5478 | 2.6716 | 2.6567 | 2.6095 | 2.4314 | 2.2991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5478 | 2.6716 | 2.6567 | 2.6095 | 2.4314 | 2.2991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BATTERSBY LA T1 / RYLANDS ELDON ST T2 | 6 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEAUMARIS T1 / BEAUMARIS T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.2973 | 10.3635 | 10.3783 | 10.344 | 10.3643 | 10.4177 | 9.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2973 | 10.3635 | 10.3783 | 10.344 | 10.3643 | 10.4177 | 9.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEAUMONT ST T1 / DINGLE VALE T1 / LARK LA T1 / MDHB BRUNSWICK DOCK T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEDBURN DV T1 / BLUEBELL LA T1 / BROOKBRIDGE T1 / ECCLESTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEECH ST T1 / LISTER DV A T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEMROSE T1 / CARR LA EAST T1 / LUCAS (FAZAKERLEY) T1 / NORRIS GREEN T1 / WEST DERBY T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 3.6551 | 3.6481 | 3.5909 | 3.462 | 3.3208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2394 | 5.4344 | 5.2538 | 4.8215 | 4.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BENTINCK ST T1 / BENTINCK ST T2 / CHESTER ST T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BERSHAM COLLIERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 4.4247 | 4.4529 | 4.4426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4247 | 4.4529 | 4.4426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BERSHAM RD T1 / IND COOPE T1 / RHYD BROUGHTON LA T1 / TUTTLE ST T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 3.4097 | 3.5388 | 3.5081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4097 | 3.5388 | 3.5081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BETHESDA T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BETWS-Y-COED T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 9.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BEWSEY T1 / OWEN ST T1 / RODNEY ST T1 / RYLANDS ELDON ST T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 3.7892 | 3.9268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7892 | 3.9268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BIBBYS T1 / INLAND REVENUE OFFICES T1 / REGENT RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BICC HUYTON QUARRY T1 / TARBOCK T1 / WHISTON T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BICC WREXHAM T1 / MARCHWIEL T1 / WIE CENTRAL T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 2.7472 | 2.4954 | 2.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7472 | 2.4954 | 2.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BIRKENHEAD CENTRAL T1 / SINGLETON AVE T1 / TRANMERE T1 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ex BIXTETH ST T1 / LITTLEWOODS T1 / PALL MALL T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLACON T1 / COCOA BARRY T1 / CRANE BANK T1 / KNUTSFORD WAY T1 / TOWER WHARF T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLAENAU FFESTINIOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLUNDELL ST T1 / ROPEWALKS T1 / ST JAMES T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BLUNDELLSANDS (NORTH) T1 / BLUNDELLSANDS (SOUTH) T1 / CROSBY T1 / KERSHAW AVE T1 / WATERLOO T2 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 3.6144 | 3.5996 | 3.5328 | 3.3797 | 3.2084 | 3.028 | 2.8281 | 2.6314 | 2.4186 | 2.1891 | 0 | 0 | 0 | 0 | 0 | 5.6869 | 5.8792 | 5.6546 | 5.097 | 4.6125 | 4.3345 | 4.0471 | 3.8468 | 3.6597 | 3.4661 | 0 | 0 | 0 | 0 | 0
| BODFARI PRODUCERS T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOLTON ST T1 / GREEK ST T1 / HPO COPPERAS HILL T1 / OLDHAM PLACE T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GRID T1 / KELLOGGS T1 / PACIFIC RD T1 / WASHINGTON ST T1 / WATERLOO T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GRID T2 / ORRELL MOUNT T1 / SCARISBRICK AVE T1 / TATTON RD T1 | 11 | BOOTLE GT1 / LITHERLAND GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOTWNNOG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOULEVARD T1 / CHAPELFORD T1 / HAWLEYS LA T1 / WESTBROOK T1 / WINWICK QUAY T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.9326 | 1.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9672 | 4.1417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOW ST T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 6.4873 | 6.375 | 6.1976 | 5.9535 | 5.7859 | 5.6765 | 5.6264 | 5.4936 | 5.2527 | 4.7257 | 4.1682 | 3.092 | 0.70953 | 0 | 0 | 6.4873 | 6.375 | 6.1976 | 5.9535 | 5.7859 | 5.6765 | 5.6264 | 5.4936 | 5.2527 | 4.7257 | 4.1682 | 3.092 | 0.70953 | 0 | 0
| BOWATER CONTAINERS T1 / ELLESMERE PORT LOCAL T1 / HH ROBERTSONS T1 / MOBIL OIL (E PORT) T1 / WHITBY T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BR STATION T1 / DUCHY RD T1 / ELECTRA WAY T1 / MIDLAND ROLLMAKERS T1A / NORTH WESTERN MILLS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH ALUMINIUM LATCHFORD T1 / GREENHALL WHITLEY T1 / LATCHFORD T1 / LATCHFORD T2 / THAMES BOARD MILL T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 1.7948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH OXYGEN T1 / WINDLEHURST T1 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0.36383 | 0.43117 | 0.41459 | 0.16186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36383 | 0.43117 | 0.41459 | 0.16186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH PIPE ASSOCIATION T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRITISH SIDAC T1 / SHERDLEY RD T1 / ST HELENS LINKWAY T1 / WATERY LA T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROADGREEN T1 / CROXTETH T1 / EAST PRESCOT RD (FINCH LA) T1 / KNOTTY ASH T1 / LEYFIELD RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMFIELD T1 / BROMFIELD T2 / PONTERWYL T1 / RHYD-Y-GOLEU T1 / SYNTHITE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 3.262 | 3.2487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3332 | 4.4405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROOK LA T1 / MANNINGS LA T1 / NEWTOWN CHESTER T1 / UPTON HEATH T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROOK ST T1 / KINGSWAY TUNNEL T1 / NWWA SANDON DOCK T1 / NWWA SANDON DOCK T2 | 11 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRYN STANLEY T1 / DENBIGH T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUCKINGHAM ST T1 / EVERTON RD T1 / SUBURBAN RD T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUCKLEY T1 / BUCKLEY T2 / BUCKLEY CROSS T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0.87167 | 0.94957 | 0.83505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87167 | 0.94957 | 0.83505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUILDWAS RD T1 / MORGAN REFRACTORIES T1 / NESTON MAIN T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 1.9597 | 2.057 | 1.7937 | 1.1515 | 0.75182 | 0.52353 | 0.38912 | 0.2953 | 0.23085 | 0.11523 | 0 | 0 | 0 | 0 | 0 | 1.9597 | 2.057 | 1.7937 | 1.1515 | 0.75182 | 0.52353 | 0.38912 | 0.2953 | 0.23085 | 0.11523 | 0 | 0 | 0 | 0 | 0
| BURLINGTON AVE T1 / FRESHFIELD T1 / MARSH BROWS T1 / SOUTHPORT RD T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 1.7919 | 1.9301 | 1.7238 | 1.2375 | 0.70085 | 0.31161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7919 | 1.9301 | 1.7238 | 1.2375 | 0.70085 | 0.31161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BURMAH OIL T1 / CABOT CARBON T1 / VAN LEER NO 1 T1 | 7 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.71032 | 0.73805 | 0.76452 | 0.74183 | 0.70761 | 0.69135 | 0.66542 | 0.64991 | 0.64762 | 0.6247 | 0.62291 | 0.71229 | 0.99826 | 1.0624 | 0.97332 | 0.71032 | 0.73805 | 0.76452 | 0.74183 | 0.70761 | 0.69135 | 0.66542 | 0.64991 | 0.64762 | 0.6247 | 0.62291 | 0.71229 | 0.99826 | 1.0624 | 0.97332
| BUTLINS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 3.3324 | 2.5125 | 1.3865 | 0.68382 | 0.18208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3324 | 2.5125 | 1.3865 | 0.68382 | 0.18208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BUTTINGTON CROSS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.0422 | 7.0754 | 7.0786 | 6.9902 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0422 | 7.0754 | 7.0786 | 6.9902 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BXL BROMBOROUGH T1 / TULIP T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0.4497 | 0.4991 | 0.52381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4497 | 0.4991 | 0.52381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CABLE ST T1 / GRADWELL ST T2 / OLDHAM PLACE T2 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CABLE ST T2 / CROWN COURTS T1 / GRADWELL ST T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CADBURYS KRONOSPAN T1 / CADBURYS KRONOSPAN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.5922 | 0.65095 | 0.64295 | 0.55162 | 0.43399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5922 | 0.65095 | 0.64295 | 0.55162 | 0.43399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CADBURYS T1 / CADBURYS T2 / HOPFIELD RD T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAERGEILIOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.34479 | 0.40115 | 0.3757 | 0.28041 | 0.2733 | 0.24534 | 0.20577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34479 | 0.40115 | 0.3757 | 0.28041 | 0.2733 | 0.24534 | 0.20577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAERGWRLE T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0.62167 | 0.69985 | 0.61657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62167 | 0.69985 | 0.61657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAERNARFON T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0.029175 | 0.068543 | 0.024546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035054 | 0.32466 | 0.38781 | 0 | 0 | 0.029175 | 0.068543 | 0.024546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035054 | 0.32466 | 0.38781 | 0 | 0
| CAERSWS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9557 | 6.3065 | 6.1454 | 5.8906 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9557 | 6.3065 | 6.1454 | 5.8906 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CALDY T1 / HOYLAKE T1 / MEOLS T1 / WEST KIRBY SOUTH T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 4.0572 | 4.2038 | 4.0416 | 3.6798 | 3.3339 | 3.1148 | 2.8689 | 2.6274 | 2.4919 | 2.3872 | 2.1959 | 2.0797 | 0 | 0 | 0 | 4.0572 | 4.2038 | 4.0416 | 3.6798 | 3.3339 | 3.1148 | 2.8689 | 2.6274 | 2.4919 | 2.3872 | 2.1959 | 2.0797 | 0 | 0 | 0
| CARBORUNDUM T1 / HOUGHTONS LA T1 / RAINFORD T1 / WINDLEHURST T2 | 11 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0.023834 | 0.17454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023834 | 0.17454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CARLTON ST T1 / CARLTON ST T2 / CHALON WAY T2 | 7 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CARMEL T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.9274 | 2.2905 | 2.1156 | 1.9 | 1.4701 | 1.1417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9274 | 2.2905 | 2.1156 | 1.9 | 1.4701 | 1.1417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | 11 | CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | Yes | 2037 | 3.0747 | 1.9409 | 1.9173 | 1.8161 | 1.6943 | 1.5833 | 1.4241 | 1.2612 | 1.1061 | 0.93422 | 0.76441 | 0.22754 | 0 | 0 | 0 | 4.5072 | 3.7269 | 3.6133 | 3.2863 | 2.7512 | 2.3281 | 1.9358 | 1.5506 | 1.2074 | 0.94842 | 0.80723 | 0.76456 | 0 | 0 | 0
| CEFN MAWR T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0.044175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CEMAES BAY T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 3.2823 | 3.3175 | 3.3157 | 3.2684 | 3.2665 | 3.2467 | 3.2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2823 | 3.3175 | 3.3157 | 3.2684 | 3.2665 | 3.2467 | 3.2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CEMMAES RD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.8189 | 2.662 | 2.4889 | 2.3013 | 2.1691 | 2.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8189 | 2.662 | 2.4889 | 2.3013 | 2.1691 | 2.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CEREAL PARTNERS T1 / LEVER GEORGIA AVE T1 / POOL LA T1 / UML LEVER BROMBOROUGH T2 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHALON WAY T1 / TECHNOLOGY CAMPUS T1 / WOODVILLE ST T1 | 7 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 1.1613 | 1.2186 | 1.217 | 0.94067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1613 | 1.2186 | 1.217 | 0.94067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESHIRE GREEN T1 / NWF T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESTER GATES T1 / UNILEVER DUNKIRK T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESTER ST (WREXHAM) T1 / EAGLES MEADOW T1 / RHOSNESNI T1 / WHITEGATE T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 3.4147 | 3.5424 | 3.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4147 | 3.5424 | 3.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHILDWALL T1 / CHILDWALL FIVEWAYS T1 / LYNDENE RD T1 / MIDDLEMASS HEY T1 / NAYLORS RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHOWLEY T1 / CHOWLEY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 10.1997 | 10.2822 | 10.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1997 | 10.2822 | 10.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHURCH LA T1 / NANT HALL T1 / PRESTATYN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 2.4967 | 2.5776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 2.5776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHURCH LAWTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHURCH ST WINSFORD T1 / OVER T1 / WHARTON PK T1 / WOODFORD PK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 4.2572 | 4.4212 | 4.2901 | 3.9475 | 3.46 | 3.2379 | 3.0278 | 2.8665 | 2.7409 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2572 | 4.4212 | 4.2901 | 3.9475 | 3.46 | 3.2379 | 3.0278 | 2.8665 | 2.7409 | 0 | 0 | 0 | 0 | 0 | 0
| CIVIC CENTRE T1 / CLAUGHTON AVE T1 / ELECTRICITY ST T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLEDFORD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLOCKFACE T1 / GEC ST HELENS T1 / HILLS MOSS T1 / NCB SUTTON MANOR T2 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLUBMOOR T1 / DUNLOPS WALTON T1 / WALTON T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CLUBMOOR T2 / LISTER DV A T1 / SUBURBAN RD T2 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COEDPOETH T1 / COEDPOETH T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.3947 | 7.4658 | 7.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3947 | 7.4658 | 7.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COLWYN BAY T1 / COLWYN BAY T2 / RHOS-ON-SEA T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 1.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONEY GREEN T1 / OSWESTRY T2 / OSWESTRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 2.3897 | 1.607 | 0.57461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3897 | 1.607 | 0.57461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONIX T1 / CONIX T2 / MEDEVA T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONNAHS QUAY LOCAL T1 / CONNAHS QUAY LOCAL T2 / HAWARDEN T1 / KING GEORGE ST T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 3.3392 | 3.2504 | 2.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3392 | 3.2504 | 2.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CONWY T1 / DEGANWY T1 / LLANDUDNO JUNCTION T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CORWEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 7.0154 | 6.6732 | 6.4867 | 6.2996 | 6.075 | 6.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0154 | 6.6732 | 6.4867 | 6.2996 | 6.075 | 6.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CREWE T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CRIGGION RADIO STATION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 2.9797 | 2.5616 | 2.3817 | 2.1451 | 1.9729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9797 | 2.5616 | 2.3817 | 2.1451 | 1.9729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CROSSFIELDS T1 / CROSSFIELDS T2 / LEVERS CROSSFIELDS T3 / GATEWARTH SEWAGE T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 0.94469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CROWTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.22532 | 0.093437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22532 | 0.093437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CWM DYLI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.0724 | 1.8097 | 1.636 | 1.4187 | 1.2588 | 1.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0724 | 1.8097 | 1.636 | 1.4187 | 1.2588 | 1.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DAILY POST & ECHO T1 / DAILY POST & ECHO T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DARESBURY NPL T1 / DARESBURY NPL T2 / DARESBURY PK T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0.59032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DAVY WAY T1 / LLAY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE ALUMINIUM T1 / DUNLOP PLASTICS T1 / FIRESTONE T1 / TETRAPAK T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.9882 | 7.9839 | 7.9828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.14 | 8.2749 | 8.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE IND PK T1 / DEESIDE IND PK 6TH AVE T1 / RAF SEALAND T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | Yes | 2037 | 2.4077 | 2.5037 | 2.563 | 2.6069 | 2.6042 | 2.6362 | 2.6205 | 2.702 | 2.7801 | 2.8921 | 3.0042 | 3.539 | 4.1607 | 3.8922 | 3.5925 | 2.4077 | 2.5037 | 2.563 | 2.6069 | 2.6042 | 2.6362 | 2.6205 | 2.702 | 2.7801 | 2.8921 | 3.0042 | 3.539 | 4.1607 | 3.8922 | 3.5925
| DELAMORE ST T1 / KIRKDALE T1 / WALTON T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DESOTO RD T1 / MERSEY BRIDGE T1 / PITT ST T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 0.73859 | 0.76219 | 0.56789 | 0 | 0 | 0 | 0.034429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73859 | 0.76219 | 0.56789 | 0 | 0 | 0 | 0.034429 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DIBBINSDALE T1 / PLYMYARD T1 / WIBP HARDKNOTT RD T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 2.4447 | 2.5363 | 2.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4447 | 2.5363 | 2.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DINGLE T1 / GRANBY T1 / ST JAMES T2 | 6 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DITTON T1 / GAVIN RD T1 / HOUGH GREEN T1 / RTZ T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 4.2368 | 4.1173 | 3.7166 | 0 | 0 | 0 | 2.502 | 2.28 | 2.1447 | 1.9682 | 1.8046 | 0.27582 | 0 | 0 | 0 | 4.2368 | 4.1173 | 3.7166 | 0 | 0 | 0 | 2.502 | 2.28 | 2.1447 | 1.9682 | 1.8046 | 0.27582 | 0 | 0
| DODDS LA T1 / HOLBORN HILL T1 / MAGHULL T1 / MAGHULL T2 / ROBBINS BRIDGE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 3.5594 | 3.5285 | 3.4396 | 3.2413 | 3.0152 | 2.7681 | 2.5098 | 2.1935 | 1.663 | 1.2848 | 0 | 0 | 0 | 0 | 0 | 6.2994 | 6.4864 | 6.0813 | 5.2176 | 4.177 | 3.5047 | 2.8464 | 2.1935 | 1.663 | 1.2848 | 0 | 0 | 0 | 0 | 0
| DOLGARROG T1 / DOLGARROG T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DOLGELLAU T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 8.9984 | 9.0833 | 9.0619 | 9.0282 | 9.0442 | 9.1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9984 | 9.0833 | 9.0619 | 9.0282 | 9.0442 | 9.1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DUCKINGTON T1 / DUCKINGTON T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DUDDON T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DYFFRYN ARDUDWY T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.8374 | 9.6177 | 9.4921 | 9.3792 | 9.3069 | 9.3361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8374 | 9.6177 | 9.4921 | 9.3792 | 9.3069 | 9.3361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DYSERTH RD T1 / FFORDD LAS T1 / FFORDD LAS T2 / WESTBOURNE AVE T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 5.3492 | 5.5388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3492 | 5.5388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EDEN VALE T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 7.0847 | 7.1356 | 7.077 | 6.8431 | 6.6005 | 6.3914 | 6.2367 | 6.0681 | 4.9124 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0847 | 7.1356 | 7.077 | 6.8431 | 6.6005 | 6.3914 | 6.2367 | 6.0681 | 4.9124 | 0 | 0 | 0 | 0 | 0 | 0
| EDERN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.07741 | 0.12746 | 0.12755 | 0.16281 | 0.1759 | 0.24568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07741 | 0.12746 | 0.12755 | 0.16281 | 0.1759 | 0.24568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EDGE HILL T1 / LIVERPOOL UNIVERSITY T1 / LIVERPOOL UNIVERSITY T2 / LIVERPOOL UNIVERSITY T3 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EDGE LA (TAPLEY PLACE) T1 / LISTER DV B T3 / MILL LA (WAVERTREE) T1 / PLESSEY (EDGE LA) T1 / STONEYCROFT T1 | 11 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EGA ELECTRIC T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 6.4292 | 6.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4292 | 6.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EGERTON T1 / ROCK FERRY T1 / SHELL TRANMERE T1 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EGREMONT T1 / LISCARD T1 / POULTON T1 / STONE MANGANESE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELLESMERE T1 / MMB ELLESMERE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELTON T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0 | 0.0061765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0061765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ENGINEER PK T1 / PILKINGTONS QUEENSFERRY T1 / QUEENSFERRY T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ESTUARY COMMERCE PK T1 / LEEWARD DR T1 / LEEWARD DR T2 / SPEKE HALL RD T1 / SPEKE SKY PK T1 | 11 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EVERTON BROW T1 / GARDNERS ROW T1 / SHEIL PK T1 | 6 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EXPRESS FOODS T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FAIRBOURNE T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 9.2548 | 9.0615 | 8.9621 | 8.8512 | 8.7437 | 8.7209 | 8.7216 | 8.7098 | 8.6825 | 8.6496 | 8.7042 | 8.7108 | 8.3314 | 1.9825 | 0 | 9.2548 | 9.0615 | 8.9621 | 8.8512 | 8.7437 | 8.7209 | 8.7216 | 8.7098 | 8.6825 | 8.6496 | 8.7042 | 8.7108 | 8.3314 | 1.9825 | 0
| FAZAKERLEY HOSPITAL T1 / JACOBS T1 / JACOBS T2 / SEEDS LA T1 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 3.3394 | 3.4688 | 3.4495 | 3.2748 | 3.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3394 | 3.4688 | 3.4495 | 3.2748 | 3.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FERODO T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.6672 | 6.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6672 | 6.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FLINT T1 / FLINT T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FODENS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORD T1 / OXTON T1 / PRENTON LOCAL T1 / SINGLETON AVE T2 | 11 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORDEN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 3.4447 | 4.6447 | 4.445 | 4.1446 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4447 | 4.6447 | 4.445 | 4.1446 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FOUR CROSSES T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRODSHAM LOCAL T1 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 0.79532 | 0.90182 | 0.85267 | 0.70473 | 0.54948 | 0.4471 | 0.36407 | 0.29047 | 0.21374 | 0.13362 | 0 | 0 | 0 | 0 | 0 | 0.79532 | 0.90182 | 0.85267 | 0.70473 | 0.54948 | 0.4471 | 0.36407 | 0.29047 | 0.21374 | 0.13362 | 0 | 0 | 0 | 0 | 0
| GADBROOK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 6.9272 | 6.9691 | 6.9342 | 6.7332 | 6.5473 | 6.422 | 6.2949 | 6.2103 | 4.9124 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9272 | 6.9691 | 6.9342 | 6.7332 | 6.5473 | 6.422 | 6.2949 | 6.2103 | 4.9124 | 0 | 0 | 0 | 0 | 0 | 0
| GAERWEN VIEW T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 9.7898 | 9.8039 | 9.7955 | 9.7516 | 9.7294 | 9.7227 | 9.7203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7898 | 9.8039 | 9.7955 | 9.7516 | 9.7294 | 9.7227 | 9.7203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GIGG LA THELWALL T1 / HILLCLIFFE T1 / STOCKTON HEATH T1 / STRETTON IND EST T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 4.8247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GILBROOK DOCK T1 / HILL RD T1 / MOBIL OIL (WALLASEY) T1 | 7 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GLAN-YR-AFON T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.35791 | 0.14279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35791 | 0.14279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GRAIG FAWR T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 8.0917 | 8.1628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0917 | 8.1628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GRAVEL T1 / WCB PLASTICS T1 / WHARTON T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 1.0897 | 1.161 | 1.1751 | 1.0488 | 0.88153 | 0.78341 | 0.68009 | 0.59777 | 0.55265 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0897 | 1.161 | 1.1751 | 1.0488 | 0.88153 | 0.78341 | 0.68009 | 0.59777 | 0.55265 | 0 | 0 | 0 | 0 | 0 | 0
| GREASBY T1 / SAUGHALL MASSIE T1 / UPTON T1 | 11 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | Yes | 2037 | 2.7557 | 2.879 | 2.7502 | 2.4572 | 2.058 | 1.8381 | 1.5898 | 1.4837 | 1.3115 | 1.1906 | 1.0611 | 0.84437 | 0 | 0 | 0 | 2.7557 | 2.879 | 2.7502 | 2.4572 | 2.058 | 1.8381 | 1.5898 | 1.4837 | 1.3115 | 1.1906 | 1.0611 | 0.84437 | 0 | 0 | 0
| GREAT SANKEY T1 / PENKETH T1 / WIDNES RD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 2.1397 | 2.2215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1397 | 2.2215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GREAT SUTTON T1 / LITTLE SUTTON T1 / STRAWBERRY ROUNDABOUT T1 / SUTTON HALL WWB T1 / WHITBY MAIN T2 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GREENFIELD T1 / GREENFIELD T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GROSVENOR ST T1 / LINENHALL ST T1 / NORTHGATE TERRACE T1 / STATION VIEW T1 / TOMULAR PLACE T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GWERSYLLT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 9.8597 | 9.9007 | 9.8636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8597 | 9.9007 | 9.8636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HALTON RD T1 / MURDISHAW T1 / PERCIVAL LA T4 / RUNCORN CENTRAL T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARLECH T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 6.8699 | 6.8361 | 6.8491 | 6.832 | 6.8122 | 6.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8699 | 6.8361 | 6.8491 | 6.832 | 6.8122 | 6.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARRINGTON ST T1 / PARADISE ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARRINGTON ST T2 / HIGHFIELD ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARRINGTON ST T3 / LIME ST T1 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARTFORD T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0.022192 | 0.1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022192 | 0.1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HASKAYNE T1 | 11 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HATHERTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HERONS WAY T1 / LACHE T1 / MBNA T1 / SMFS KINGSMEADOW T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HIGHFIELD ST T2 / LIME ST T2 / OLD HAYMARKET T1 | 11 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLMES CHAPEL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLT LA (WARRINGTON RD) T1 / PRESCOT T1 / RAINHILL LOCAL T1 / WHISTON HOSP T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 4.9074 | 4.7681 | 4.3313 | 0 | 0 | 0 | 2.5076 | 2.2504 | 1.9671 | 1.6403 | 1.0971 | 0 | 0 | 0 | 0 | 4.9074 | 4.7681 | 4.3313 | 0 | 0 | 0 | 2.5076 | 2.2504 | 1.9671 | 1.6403 | 1.0971 | 0 | 0 | 0
| HOLWAY RD T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 7.5997 | 7.6398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5997 | 7.6398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLYHEAD T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.024788 | 0.061242 | 0.080796 | 0.053525 | 0.068902 | 0.10884 | 0.14791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024788 | 0.061242 | 0.080796 | 0.053525 | 0.068902 | 0.10884 | 0.14791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLYWELL T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.18917 | 0.27668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18917 | 0.27668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOOTON MAIN T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HUNTS CROSS T1 / KENTON RD T1 / WOODEND AVE T1 / WOOLTON T1 | 11 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HUYTON HEY RD T1 / WILSON RD T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IFTON T1 / IFTON T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.5172 | 7.5753 | 7.5416 | 7.3972 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5172 | 7.5753 | 7.5416 | 7.3972 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ILFORDS T1 / KNUTSFORD T1 / MOBBERLEY T1 / RADBROKE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 1.5195 | 1.6759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5195 | 1.6759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IVY ST (SOUTHPORT) T1 / KENSINGTON RD T1 / MARKET ST T1 / SOUTHPORT T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 3.1744 | 3.3049 | 3.3642 | 3.286 | 3.1475 | 3.1205 | 3.0274 | 3.0189 | 3.0383 | 3.0849 | 3.1163 | 3.8502 | 0 | 0 | 0 | 3.1744 | 3.3049 | 3.3642 | 3.286 | 3.1475 | 3.1205 | 3.0274 | 3.0189 | 3.0383 | 3.0849 | 3.1163 | 3.8502 | 0 | 0 | 0
| IVY ST T1 / LLYSFAEN RD T1 / OLD MILL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| JOHNSTOWN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 7.6097 | 7.6625 | 7.689 | 7.6268 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6097 | 7.6625 | 7.689 | 7.6268 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KELCO T1 / NEWS INTERNATIONAL T1 / NEWS INTERNATIONAL T2 / PALCO T1 / SOUTHDENE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KINGSLAND 33 T1 / SAFEWAY T1 / WOOLSTON T1 / WOOLSTON T2 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 3.5772 | 3.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5772 | 3.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KINNERTON T1 | 11 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | Yes | 2037 | 9.9817 | 10.0228 | 4.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9817 | 10.0228 | 4.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KIRKBY CENTRAL T1 / NORTHWOOD T1 / TOWER HILL (BANK LA) T1 / WESTVALE T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KNOWSLEY T1 / MARLED HEY T1 | 11 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KNUTSFORD T2 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 1.3618 | 1.3724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3618 | 1.3724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LCWW HUNTINGTON T1 / LCWW HUNTINGTON T2 | 7 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEA GREEN T1 / PILKINGTONS HO T1 / RAVENHEAD RETAIL PK T1 / SOMERFIELD DISTRIBUTION T1 | 11 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEGACY LOCAL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 4.1997 | 4.2293 | 4.1879 | 4.0546 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1997 | 4.2293 | 4.1879 | 4.0546 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEIGHTON HOSP T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LIVERPOOL RD 33 T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 4.5272 | 4.5719 | 4.5703 | 4.4468 | 4.3551 | 4.3404 | 4.3138 | 4.2706 | 4.2625 | 4.2209 | 4.1657 | 2.3401 | 0 | 0 | 0 | 4.5272 | 4.5719 | 4.5703 | 4.4468 | 4.3551 | 4.3404 | 4.3138 | 4.2706 | 4.2625 | 4.2209 | 4.1657 | 2.3401 | 0 | 0 | 0
| LLAINGOCH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.14729 | 0.18083 | 0.14516 | 0.10167 | 0.12034 | 0.12811 | 0.19538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14729 | 0.18083 | 0.14516 | 0.10167 | 0.12034 | 0.12811 | 0.19538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANARMON T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 9.5567 | 9.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5567 | 9.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANBEDROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.3024 | 8.5302 | 7.8288 | 6.0409 | 4.4288 | 3.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3024 | 8.5302 | 7.8288 | 6.0409 | 4.4288 | 3.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANBERIS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 6.3392 | 6.2565 | 6.2497 | 6.1831 | 6.1195 | 6.1251 | 6.1055 | 6.1044 | 6.1265 | 6.1485 | 6.1893 | 6.4522 | 6.3535 | 5.7096 | 5.182 | 6.3392 | 6.2565 | 6.2497 | 6.1831 | 6.1195 | 6.1251 | 6.1055 | 6.1044 | 6.1265 | 6.1485 | 6.1893 | 6.4522 | 6.3535 | 5.7096 | 5.182
| LLANDDEUSANT T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDDU QUARRY T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 1.3397 | 1.337 | 1.2897 | 0.90416 | 0.41862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3397 | 1.337 | 1.2897 | 0.90416 | 0.41862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDEGFAN T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 6.4183 | 6.4462 | 6.4092 | 6.3041 | 6.1964 | 6.1112 | 6.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4183 | 6.4462 | 6.4092 | 6.3041 | 6.1964 | 6.1112 | 6.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDRINIO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 3.1122 | 2.916 | 2.7155 | 2.4294 | 2.2196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1122 | 2.916 | 2.7155 | 2.4294 | 2.2196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDUDNO T1 / LLANDUDNO T2 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 1.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDYFRYDOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.4398 | 7.2236 | 7.0168 | 6.7873 | 6.3038 | 5.6103 | 4.8634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4398 | 7.2236 | 7.0168 | 6.7873 | 6.3038 | 5.6103 | 4.8634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANDYRNOG T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFAELOG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 4.0298 | 4.0782 | 4.0906 | 4.0747 | 4.0542 | 4.0492 | 4.0586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0298 | 4.0782 | 4.0906 | 4.0747 | 4.0542 | 4.0492 | 4.0586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFAIR CAEREINION T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 4.5122 | 4.5174 | 4.4372 | 4.2303 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5122 | 4.5174 | 4.4372 | 4.2303 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFAIR PG T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.8798 | 7.9301 | 7.8934 | 7.8103 | 7.7451 | 7.7206 | 7.7115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8798 | 7.9301 | 7.8934 | 7.8103 | 7.7451 | 7.7206 | 7.7115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFAIRFECHAN T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 6.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFROTHEN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.2174 | 9.1282 | 9.1323 | 9.1235 | 9.1395 | 9.1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2174 | 9.1282 | 9.1323 | 9.1235 | 9.1395 | 9.1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFWROG T1 / RUTHIN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANFYLLIN T1 / LLANFYLLIN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANGAFFO T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 7.5698 | 7.3695 | 7.1518 | 6.9064 | 6.6704 | 6.5048 | 6.1809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5698 | 7.3695 | 7.1518 | 6.9064 | 6.6704 | 6.5048 | 6.1809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANGEFNI IND EST T1 / LLANGEFNI IND EST T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 1.4523 | 1.2826 | 1.1648 | 1.0065 | 0.45168 | 0.047935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4523 | 1.2826 | 1.1648 | 1.0065 | 0.45168 | 0.047935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANGEFNI T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.2298 | 10.2627 | 10.2396 | 10.1829 | 10.1188 | 10.1134 | 9.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2298 | 10.2627 | 10.2396 | 10.1829 | 10.1188 | 10.1134 | 9.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANGOLLEN T1 / LLANGOLLEN T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.2397 | 0.32695 | 0.2878 | 0.15364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2397 | 0.32695 | 0.2878 | 0.15364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANIDLOES T1 / LLANIDLOES T2 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANILAR T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 1.9173 | 1.7159 | 1.5381 | 1.2889 | 1.0898 | 0.95674 | 0.87814 | 0.82227 | 0.6825 | 0.53774 | 0.47429 | 0.54776 | 0 | 0 | 0 | 1.9173 | 1.7159 | 1.5381 | 1.2889 | 1.0898 | 0.95674 | 0.87814 | 0.82227 | 0.6825 | 0.53774 | 0.47429 | 0.54776 | 0 | 0 | 0
| LLANRWST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 7.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANSANNAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 9.8467 | 9.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8467 | 9.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLANSILIN T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 8.4982 | 8.307 | 8.1014 | 7.8116 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4982 | 8.307 | 8.1014 | 7.8116 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LLYNCLYS T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9777 | 7.0417 | 6.8433 | 6.5037 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9777 | 7.0417 | 6.8433 | 6.5037 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LORD ST T1 / MARSHSIDE T1 / MULLARDS BALMORAL DV T1 / SOUTHPORT T2 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 3.8394 | 3.6537 | 3.2886 | 2.6257 | 2.143 | 1.7372 | 1.3439 | 0.97017 | 0.63251 | 0.422 | 0.21905 | 0.60335 | 0 | 0 | 0 | 3.8394 | 3.6537 | 3.2886 | 2.6257 | 2.143 | 1.7372 | 1.3439 | 0.97017 | 0.63251 | 0.422 | 0.21905 | 0.60335 | 0 | 0 | 0
| LOSTOCK T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LOSTOCK TRIANGLE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 9.1922 | 9.2338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1922 | 9.2338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LOWER BEBINGTON T1 / NEW FERRY T1 / SPITAL T1 / UNILEVER RESEARCH T1 | 11 | BROMBOROUGH GT3 / ROCK FERRY GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LUGSDALE T1 / PILK SULLIVAN T1 / PILK SULLIVAN T2 / USAC T1 | 11 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | Yes | 2037 | 0 | 2.2361 | 2.2642 | 2.1186 | 0 | 0 | 0 | 1.5815 | 1.5223 | 1.3945 | 1.318 | 1.3843 | 1.6279 | 0 | 0 | 0 | 2.2361 | 2.2642 | 2.1186 | 0 | 0 | 0 | 1.5815 | 1.5223 | 1.3945 | 1.318 | 1.3843 | 1.6279 | 0 | 0
| LYMM T1 / WHITELEGGS LA T1 | 11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | Yes | 2037 | 1.2072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MACHYNLLETH T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 3.2828 | 3.3673 | 3.3617 | 3.3299 | 3.3401 | 3.4042 | 3.4591 | 3.5266 | 3.6655 | 3.7553 | 3.8587 | 4.3951 | 4.811 | 4.4565 | 4.165 | 3.2828 | 3.3673 | 3.3617 | 3.3299 | 3.3401 | 3.4042 | 3.4591 | 3.5266 | 3.6655 | 3.7553 | 3.8587 | 4.3951 | 4.811 | 4.4565 | 4.165
| MACHYNLLETH T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 4.3976 | 4.0301 | 3.7846 | 3.4977 | 3.2634 | 3.0997 | 3.001 | 2.9128 | 2.8099 | 2.7049 | 2.6573 | 2.5448 | 2.0664 | 0 | 0 | 4.3976 | 4.0301 | 3.7846 | 3.4977 | 3.2634 | 3.0997 | 3.001 | 2.9128 | 2.8099 | 2.7049 | 2.6573 | 2.5448 | 2.0664 | 0 | 0
| MAELOR CREAMERY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 9.3797 | 9.162 | 9.0125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3797 | 9.162 | 9.0125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MAENTWROG T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.1949 | 8.9533 | 8.8048 | 8.6191 | 8.5036 | 8.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1949 | 8.9533 | 8.8048 | 8.6191 | 8.5036 | 8.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MAES-Y-CLAWDD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 5.9347 | 5.9742 | 5.9971 | 5.9401 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9347 | 5.9742 | 5.9971 | 5.9401 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MANOD T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 2.7729 | 2.5598 | 2.4037 | 2.2447 | 2.1261 | 2.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7729 | 2.5598 | 2.4037 | 2.2447 | 2.1261 | 2.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MANOR PK T1 / NORTON CHAINS T1 | 11 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | Yes | 2037 | 2.0378 | 2.2572 | 2.4141 | 2.2436 | 1.9733 | 1.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0378 | 2.2572 | 2.4141 | 2.2436 | 1.9733 | 1.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MDHB EGERTON DOCK T1 / MDHB EGERTON DOCK T2 | 7 | PRENTON GRID GT1 / ROCK FERRY GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MERE T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.9497 | 7.0182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9497 | 7.0182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MERES EDGE T1 / MERES EDGE T2 | 11 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | Yes | 2037 | 10.4053 | 9.8293 | 3.4331 | 10.3147 | 10.2594 | 10.2343 | 10.2091 | 10.179 | 10.2103 | 10.2185 | 10.1819 | 10.3775 | 9.8723 | 8.3318 | 6.8968 | 10.4053 | 9.8293 | 3.4331 | 10.3147 | 10.2594 | 10.2343 | 10.2091 | 10.179 | 10.2103 | 10.2185 | 10.1819 | 10.3775 | 9.8723 | 8.3318 | 6.8968
| MIDDLEWICH T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MIDPOINT POCHIN WAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 8.9122 | 8.9236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9122 | 8.9236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MILFORD T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MINFFORDD T1 / PARC BRYN CEGIN T1 / PARC BRYN CEGIN T2 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 1.0717 | 1.1094 | 1.099 | 1.027 | 0.96867 | 0.97159 | 0.95672 | 0.97156 | 1.0055 | 0.99846 | 1.0125 | 1.1909 | 1.0699 | 0.67288 | 0 | 1.0717 | 1.1094 | 1.099 | 1.027 | 0.96867 | 0.97159 | 0.95672 | 0.97156 | 1.0055 | 0.99846 | 1.0125 | 1.1909 | 1.0699 | 0.67288 | 0
| MOCHDRE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 6.9472 | 6.7782 | 6.6863 | 6.4966 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9472 | 6.7782 | 6.6863 | 6.4966 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MONA T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 5.2973 | 3.1496 | 3.1054 | 2.9563 | 2.8678 | 2.8943 | 2.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2973 | 3.1496 | 3.1054 | 2.9563 | 2.8678 | 2.8943 | 2.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MONSANTO T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MORDA T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 8.8697 | 4.6936 | 4.8646 | 5.1075 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8697 | 4.6936 | 4.8646 | 5.1075 | 2.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MORGANITE CERAMICS T1 / PLYMYARD T2 / VAUXHALL NORTH RD T1 | 11 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MORRISONS T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 7.3172 | 7.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3172 | 7.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NANTWICH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NANT-Y-GAMAR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 0.35917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NEVILL ST T1 / OCEAN PLAZA T1 / YORK RD T1 | 11 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | Yes | 2037 | 1.9769 | 2.052 | 2.0994 | 1.9931 | 1.8664 | 1.7942 | 1.7051 | 1.6399 | 1.5723 | 1.5858 | 1.6512 | 2.1876 | 0 | 0 | 0 | 1.9769 | 2.052 | 2.0994 | 1.9931 | 1.8664 | 1.7942 | 1.7051 | 1.6399 | 1.5723 | 1.5858 | 1.6512 | 2.1876 | 0 | 0 | 0
| NEW BRIGHTON T1 / SEAVIEW RD T2 / WALLASEY T1 / WALLASEY VILLAGE T1 | 11 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NEWHALL T1 / NEWHALL T2 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NORTH WALES PAPER T1 / NORTH WALES PAPER T2 / WOODFIELD AVE T1 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 3.2592 | 3.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2592 | 3.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NORTH WEST WATER CAMPUS T1 / NORTH WEST WATER CAMPUS T2 / OMEGA T1 / OMEGA T2 / ORION BOULEVARD T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OPTICAL FIBRES T1 / SHOTWICK T1 / WALBRO T1 | 11 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | Yes | 2037 | 1.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ORB CL T1 / STONEBRIDGE LA T1 / STONEBRIDGE LA T2 | 11 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | Yes | 2037 | 0.16693 | 0.22778 | 0.23663 | 0.070225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16693 | 0.22778 | 0.23663 | 0.070225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ORFORD T1 / PADGATE T1 | 11 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | Yes | 2037 | 1.1822 | 1.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1822 | 1.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OTIS ELEVATOR T1 / ST IVEL FOODS T1 | 11 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OVERTON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0.4847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PANDY T1 / PANDY T2 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 1.0672 | 1.1642 | 1.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0672 | 1.1642 | 1.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PARC CYBI T1 / PARC CYBI T2 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 0.57979 | 0.60636 | 0.60746 | 0.60007 | 0.59659 | 0.59455 | 0.59496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57979 | 0.60636 | 0.60746 | 0.60007 | 0.59659 | 0.59455 | 0.59496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PARC MENAI T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 7.0417 | 7.0587 | 7.0424 | 6.9701 | 6.9484 | 6.9142 | 6.9285 | 6.9132 | 6.9024 | 6.9343 | 6.9327 | 6.9514 | 6.9839 | 6.7905 | 6.6301 | 7.0417 | 7.0587 | 7.0424 | 6.9701 | 6.9484 | 6.9142 | 6.9285 | 6.9132 | 6.9024 | 6.9343 | 6.9327 | 6.9514 | 6.9839 | 6.7905 | 6.6301
| PEBLIC MILLS T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PENMAENMAWR T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 9.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PENTRAETH T1 | 11 | AMLWCH GT1 / CAERGEILIOG GT1 | Yes | 2037 | 10.4523 | 10.5167 | 10.4739 | 10.3708 | 10.2487 | 10.1816 | 9.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4523 | 10.5167 | 10.4739 | 10.3708 | 10.2487 | 10.1816 | 9.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PEN-Y-GROES T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 3.2812 | 2.8532 | 2.8294 | 2.7551 | 2.7212 | 2.7042 | 2.6528 | 2.659 | 2.6916 | 2.7626 | 2.8055 | 3.0183 | 2.7557 | 1.7753 | 0.52087 | 3.2812 | 2.8532 | 2.8294 | 2.7551 | 2.7212 | 2.7042 | 2.6528 | 2.659 | 2.6916 | 2.7626 | 2.8055 | 3.0183 | 2.7557 | 1.7753 | 0.52087
| PILKINGTONS T1 / PILKINGTONS T2 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.53917 | 0.3295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53917 | 0.3295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| POINT OF AYR COLLIERY T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 0.45167 | 0.5129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45167 | 0.5129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PORTHMADOG T1 / PORTHMADOG T2 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 0.86741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PREES T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 9.8447 | 9.3904 | 9.0055 | 8.4967 | 7.9056 | 7.1365 | 6.7966 | 6.5846 | 6.374 | 6.1596 | 5.9533 | 2.3401 | 0 | 0 | 0 | 9.8447 | 9.3904 | 9.0055 | 8.4967 | 7.9056 | 7.1365 | 6.7966 | 6.5846 | 6.374 | 6.1596 | 5.9533 | 2.3401 | 0 | 0 | 0
| PRIMROSE HALL T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.6447 | 6.6689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6447 | 6.6689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PWLLHELI T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 7.6949 | 7.7333 | 7.7109 | 7.6536 | 7.603 | 7.6219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6949 | 7.7333 | 7.7109 | 7.6536 | 7.603 | 7.6219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RADWAY GREEN T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RAVEN SQUARE T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| REFORM ST T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 10.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHM FOODS LTD T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHOSLAN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 9.9369 | 9.9981 | 9.9942 | 9.997 | 10.0278 | 10.0958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9369 | 9.9981 | 9.9942 | 9.997 | 10.0278 | 10.0958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHUDDLAN T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 6.7042 | 6.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7042 | 6.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RHYDLYDAN T2 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 1.5673 | 1.6727 | 1.6555 | 1.5606 | 1.5022 | 1.4827 | 1.4981 | 1.4892 | 1.52 | 1.5322 | 1.5329 | 1.6417 | 1.6895 | 1.3661 | 1.1979 | 1.5673 | 1.6727 | 1.6555 | 1.5606 | 1.5022 | 1.4827 | 1.4981 | 1.4892 | 1.52 | 1.5322 | 1.5329 | 1.6417 | 1.6895 | 1.3661 | 1.1979
| RHYD-Y-FOEL T1 | 11 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | Yes | 2037 | 3.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RINGWAY T1 | 11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | Yes | 2037 | 6.5372 | 6.3807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5372 | 6.3807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RIVALS T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 3.6424 | 3.334 | 3.1289 | 2.9233 | 3.9297 | 3.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6424 | 3.334 | 3.1289 | 2.9233 | 3.9297 | 3.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROLLS ROYCE T1 / ROLLS ROYCE T2 / ROLLS ROYCE T3 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROSSETT T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 8.8397 | 8.9331 | 9.1278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8397 | 8.9331 | 9.1278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROYAL INSURANCE (NEW QUAY) T1 / ROYAL INSURANCE (NEW QUAY) T2 | 6 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RUABON T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SALTNEY T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SANDBACH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SHAWBURY T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SMALLWOOD T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SNOWHILL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ST ASAPH BUSINESS PK T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 10.2974 | 10.2241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2974 | 10.2241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ST HELENS RD T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 0.21917 | 0.26085 | 0.25326 | 0.20824 | 0.12598 | 0.12849 | 0.099752 | 0.10573 | 0.12286 | 0.14615 | 0.21369 | 0.47686 | 0.37518 | 0 | 0 | 0.21917 | 0.26085 | 0.25326 | 0.20824 | 0.12598 | 0.12849 | 0.099752 | 0.10573 | 0.12286 | 0.14615 | 0.21369 | 0.47686 | 0.37518 | 0 | 0
| STAPELEY T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TACO PLASTICS T1 / TACO PLASTICS T2 / UNITED PERIPHERALS T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 1.8552 | 1.9253 | 1.9807 | 1.9752 | 1.8663 | 1.855 | 1.8245 | 1.7751 | 1.7848 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8552 | 1.9253 | 1.9807 | 1.9752 | 1.8663 | 1.855 | 1.8245 | 1.7751 | 1.7848 | 0 | 0 | 0 | 0 | 0 | 0
| TARPORLEY T1 | 11 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | Yes | 2037 | 7.0672 | 7.1151 | 7.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0672 | 7.1151 | 7.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TARVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TRYWERYN T1 | 11 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | Yes | 2037 | 4.6274 | 4.1263 | 4.0488 | 3.933 | 3.8289 | 3.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6274 | 4.1263 | 4.0488 | 3.933 | 3.8289 | 3.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TWYFORDS T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TYWYN T1 | 11 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | Yes | 2037 | 7.1823 | 7.2573 | 7.2681 | 7.2126 | 7.1718 | 7.1918 | 7.205 | 7.214 | 7.3664 | 7.5051 | 7.7125 | 8.3739 | 8.4253 | 7.1991 | 5.3278 | 7.1823 | 7.2573 | 7.2681 | 7.2126 | 7.1718 | 7.1918 | 7.205 | 7.214 | 7.3664 | 7.5051 | 7.7125 | 8.3739 | 8.4253 | 7.1991 | 5.3278
| WAENFAWR T1 | 11 | BANGOR GT2 / CAERNARFON GT2 | Yes | 2037 | 9.1077 | 8.7066 | 8.6757 | 8.6194 | 8.5844 | 8.5814 | 8.5812 | 8.5924 | 8.6187 | 8.7157 | 8.7693 | 8.6531 | 8.0302 | 0.44169 | 0 | 9.1077 | 8.7066 | 8.6757 | 8.6194 | 8.5844 | 8.5814 | 8.5812 | 8.5924 | 8.6187 | 8.7157 | 8.7693 | 8.6531 | 8.0302 | 0.44169 | 0
| WELSHPOOL T1 | 11 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEM EAST T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEM T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WERVIN T1 | 11 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEST FELTON T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 7.7672 | 7.5631 | 7.3791 | 7.0927 | 6.8766 | 6.6459 | 6.2745 | 5.9167 | 5.6232 | 5.2474 | 4.8338 | 2.3401 | 0 | 0 | 0 | 7.7672 | 7.5631 | 7.3791 | 7.0927 | 6.8766 | 6.6459 | 6.2745 | 5.9167 | 5.6232 | 5.2474 | 4.8338 | 2.3401 | 0 | 0 | 0
| WESTON T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WHEELOCK T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WHITCHURCH T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 5.7972 | 5.8408 | 5.6664 | 5.2687 | 5.0082 | 4.8736 | 4.7769 | 4.6781 | 4.6208 | 4.6397 | 4.6608 | 2.3401 | 0 | 0 | 0 | 5.7972 | 5.8408 | 5.6664 | 5.2687 | 5.0082 | 4.8736 | 4.7769 | 4.6781 | 4.6208 | 4.6397 | 4.6608 | 2.3401 | 0 | 0 | 0
| WIMPEYS PANT QUARRY T1 / WIMPEYS PANT QUARRY T2 | 11 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | Yes | 2037 | 0.68417 | 0.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68417 | 0.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WINCHAM T1 | 11 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | Yes | 2037 | 6.5697 | 6.5947 | 6.6093 | 6.4456 | 6.3048 | 6.1877 | 6.1023 | 6.0227 | 4.9124 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5697 | 6.5947 | 6.6093 | 6.4456 | 6.3048 | 6.1877 | 6.1023 | 6.0227 | 4.9124 | 0 | 0 | 0 | 0 | 0 | 0
| WISTASTON HALL T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WRENBURY FRITH T1 | 11 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| YOCKINGS GATE T1 | 11 | OSWESTRY GT5 / WHITCHURCH GT1 | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| YSBYTY GLAN CLWYD T1 | 11 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | Yes | 2037 | 5.7067 | 5.7361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7067 | 5.7361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Groups | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | 33 | SWANSEA NORTH | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 6.8433 | 2.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.2166 | 13.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | 33 | TRAWSFYNYDD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | 33 | CELLARHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | 33 | KIRKBY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | 33 | KIRKBY | Yes | 2037 | 19.5203 | 17.1399 | 14.9782 | 12.8757 | 10.7938 | 8.3232 | 5.3474 | 4.7641 | 3.8003 | 3.2817 | 2.7306 | 1.1417 | 0 | 0 | 0 | 64.7814 | 60.0948 | 55.9752 | 52.3985 | 48.5573 | 41.6159 | 26.7369 | 23.8205 | 19.0016 | 16.4087 | 13.6529 | 5.7086 | 0 | 0 | 0
| AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | 33 | KIRKBY | Yes | 2037 | 3.6894 | 2.7899 | 2.0979 | 1.4933 | 0.92767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4472 | 13.9493 | 10.4896 | 7.4663 | 4.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 5.341 | 2.73 | 0.88471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.7049 | 13.6498 | 4.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | 33 | KIRKBY | Yes | 2037 | 13.3525 | 11.625 | 10.1314 | 8.6807 | 7.3171 | 5.6582 | 4.0337 | 3.1422 | 1.9074 | 1.1289 | 0 | 0 | 0 | 0 | 0 | 63.1018 | 58.1252 | 50.6571 | 43.4034 | 36.5853 | 28.2911 | 20.1687 | 15.7111 | 9.5372 | 5.6444 | 0 | 0 | 0 | 0 | 0
| AMLWCH GT1 / CAERGEILIOG GT1 | 33 | WYLFA | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 10.8137 | 9.4118 | 8.5323 | 7.1127 | 6.2634 | 5.4059 | 4.0763 | 2.8744 | 0.98249 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0684 | 47.059 | 42.6615 | 35.5633 | 31.3172 | 27.0296 | 20.3815 | 14.3719 | 4.9124 | 0 | 0 | 0 | 0 | 0 | 0
| BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | 33 | RAINHILL | Yes | 2037 | 0 | 8.4064 | 3.296 | 1.1243 | 0 | 0 | 0 | 1.6665 | 3.1416 | 3.0827 | 1.6319 | 3.6737 | 1.1117 | 0 | 0 | 0 | 32.0101 | 16.4801 | 5.6216 | 0 | 0 | 0 | 8.3325 | 15.7078 | 15.4136 | 8.1597 | 16.1077 | 5.5587 | 0 | 0
| HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | 33 | BIRKENHEAD | Yes | 2037 | 5.9072 | 5.8311 | 5.6493 | 5.2619 | 4.9153 | 4.5107 | 3.9653 | 3.5172 | 2.9348 | 2.7384 | 2.5458 | 1.9156 | 0.98733 | 0 | 0 | 29.5361 | 29.1554 | 28.2465 | 26.3093 | 24.5767 | 22.5535 | 19.8263 | 17.586 | 14.6742 | 13.6922 | 12.7289 | 9.5778 | 4.9366 | 0 | 0
| BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | 33 | LEGACY | Yes | 2037 | 24.1408 | 16.6571 | 8.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7925 | 83.2857 | 41.9749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | 33 | CAPENHURST | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | 33 | FRODSHAM - INCE | Yes | 2037 | 10.4504 | 8.8225 | 8.0156 | 7.168 | 6.1328 | 2.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5152 | 30.0368 | 26.6289 | 23.6665 | 19.8043 | 13.4599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BANGOR GT2 / CAERNARFON GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 13.2311 | 9.0537 | 6.6756 | 2.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.2311 | 9.0537 | 6.6756 | 2.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 4.2875 | 1.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6867 | 5.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OSWESTRY GT5 / WHITCHURCH GT1 | 33 | LEGACY | Yes | 2037 | 39.3925 | 37.502 | 34.3027 | 30.8666 | 27.8387 | 24.7154 | 21.6084 | 17.8135 | 13.505 | 10.5001 | 7.5994 | 0 | 0 | 0 | 0 | 125.2148 | 119.6098 | 108.0256 | 95.7211 | 85.1628 | 74.7364 | 63.0406 | 48.113 | 30.54 | 18.7818 | 7.5994 | 0 | 0 | 0 | 0
| GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PRENTON GRID GT1 / ROCK FERRY GT1 | 33 | BIRKENHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | 33 | LISTER DRIVE | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | 33 | FRODSHAM - INCE | Yes | 2037 | 5.2937 | 1.9659 | 0.68662 | 2.2375 | 3.5647 | 3.9525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6269 | 9.8293 | 3.4331 | 7.2481 | 6.8229 | 3.9525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BOOTLE GT1 / LITHERLAND GT1A | 33 | KIRKBY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | 33 | CAPENHURST | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | 33 | LEGACY | Yes | 2037 | 13.4441 | 1.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4441 | 1.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SANKEY BRIDGES GT3 / WARRINGTON GT5 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | 33 | RAINHILL | Yes | 2037 | 4.6422 | 1.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6422 | 1.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 2.9733 | 1.7489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8663 | 8.7445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BROMBOROUGH GT3 / ROCK FERRY GT2 | 33 | BIRKENHEAD | Yes | 2037 | 6.7504 | 4.8928 | 2.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7504 | 4.8928 | 2.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | 33 | BIRKENHEAD | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | 33 | CARRINGTON - FIDDLERS FERRY | Yes | 2037 | 10.8137 | 3.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0684 | 15.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | 33 | RAINHILL | Yes | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | 33 | CONNAHS QUAY - PENTIR - ST ASAPH | Yes | 2037 | 3.327 | 10.4567 | 7.4512 | 4.7436 | 2.9207 | 0.97326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.327 | 10.4567 | 7.4512 | 4.7436 | 2.9207 | 0.97326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Substation Locations
Return to Contents
District | Substation Name | Easting | Northing
Dee Valley & Mid Wales | ABERDYFI | 260372 | 296137
Dee Valley & Mid Wales | ABERYSTWYTH | 260709 | 281284
Dee Valley & Mid Wales | AIRBUS | 335108 | 364305
Dee Valley & Mid Wales | ALLTAMI | 327440 | 366321
Dee Valley & Mid Wales | ASH ROAD | 337668 | 350532
Dee Valley & Mid Wales | B R D | 312009 | 291775
Dee Valley & Mid Wales | BALA | 293429 | 337046
Dee Valley & Mid Wales | BARMOUTH | 261016 | 316124
Dee Valley & Mid Wales | BASCHURCH | 342254 | 323437
Dee Valley & Mid Wales | BERSHAM COLLIERY | 331359 | 348034
Dee Valley & Mid Wales | BERSHAM ROAD | 332241 | 349615
Dee Valley & Mid Wales | BICC WREXHAM | 338874 | 349609
Dee Valley & Mid Wales | BOW STREET | 263087 | 285740
Dee Valley & Mid Wales | BRETTON TREATMENT WK | 335355 | 363160
Dee Valley & Mid Wales | BROMFIELD | 324336 | 362806
Dee Valley & Mid Wales | BROUGHTON RETAIL PARK | 335003 | 363750
Dee Valley & Mid Wales | BRYMBO GRID | 329055 | 353194
Dee Valley & Mid Wales | BSK ALUMINIUM | 295800 | 284385
Dee Valley & Mid Wales | BUCKLEY | 329527 | 363541
Dee Valley & Mid Wales | BUCKLEY CROSS | 327748 | 364089
Dee Valley & Mid Wales | BUTTINGTON CROSS | 323945 | 308485
Dee Valley & Mid Wales | CADBURYS - KRONOSPAN | 328396 | 338227
Dee Valley & Mid Wales | CAERGWRLE | 329624 | 358665
Dee Valley & Mid Wales | CAERSWS | 303757 | 292656
Dee Valley & Mid Wales | CASTLE PARK IND EST | 324563 | 373340
Dee Valley & Mid Wales | CEFN MAWR | 319973 | 363996
Dee Valley & Mid Wales | CEMMAES ROAD | 281817 | 304590
Dee Valley & Mid Wales | CERRIGYDRUDION | 295607 | 349160
Dee Valley & Mid Wales | CHESTER ST | 333644 | 350470
Dee Valley & Mid Wales | CLYWEDOG ROAD | 337345 | 349286
Dee Valley & Mid Wales | COEDPOETH | 328917 | 351526
Dee Valley & Mid Wales | CONEY GREEN | 329224 | 329602
Dee Valley & Mid Wales | CONNAHS QUAY | 329035 | 368884
Dee Valley & Mid Wales | CONTINENTAL CAN | 338062 | 349614
Dee Valley & Mid Wales | CORWEN | 306237 | 343413
Dee Valley & Mid Wales | CRIGGION RADIO | 327972 | 314646
Dee Valley & Mid Wales | CULFAN | 328886 | 346013
Dee Valley & Mid Wales | DAVY WAY | 332317 | 356644
Dee Valley & Mid Wales | DEESIDE ALUMINIUM | 337597 | 349245
Dee Valley & Mid Wales | DERWEN | 308188 | 350080
Dee Valley & Mid Wales | DOLGELLAU | 273689 | 317711
Dee Valley & Mid Wales | DUNLOP PLASTICS | 337775 | 349718
Dee Valley & Mid Wales | DYFFRYN ARDUDWY | 258462 | 322539
Dee Valley & Mid Wales | DYNOPLAST | 333327 | 367585
Dee Valley & Mid Wales | EAGLES MEADOW | 333843 | 350088
Dee Valley & Mid Wales | ELLESMERE | 339751 | 335291
Dee Valley & Mid Wales | ELLESMERE SOUTH | 340015 | 334169
Dee Valley & Mid Wales | EXPRESS FOODS | 338997 | 322382
Dee Valley & Mid Wales | FAIRBOURNE | 263268 | 313497
Dee Valley & Mid Wales | FFERM WYNT CEMMAES | 286300 | 305663
Dee Valley & Mid Wales | FFERM WYNT LLANGWYRYFON | 261856 | 269627
Dee Valley & Mid Wales | FFORDD PENTRE | 332329 | 367970
Dee Valley & Mid Wales | FIBREGLASS | 339410 | 350008
Dee Valley & Mid Wales | FIRESTONE | 338374 | 349176
Dee Valley & Mid Wales | FLINT | 323901 | 373412
Dee Valley & Mid Wales | FORDEN | 322442 | 299653
Dee Valley & Mid Wales | GLAN YR AFON | 302039 | 342560
Dee Valley & Mid Wales | GOBOWEN | 329683 | 333734
Dee Valley & Mid Wales | GRESFORD INDUSTRIAL ESTATE | 333942 | 353674
Dee Valley & Mid Wales | GWERSYLLT | 332039 | 353110
Dee Valley & Mid Wales | HAWARDEN | 329875 | 365976
Dee Valley & Mid Wales | HOYA GLASS | 338366 | 350311
Dee Valley & Mid Wales | IFTON | 332254 | 337264
Dee Valley & Mid Wales | IND COOPE | 333038 | 350467
Dee Valley & Mid Wales | JCB TRANSMISSION | 337944 | 350661
Dee Valley & Mid Wales | JOHNSTOWN | 330516 | 345376
Dee Valley & Mid Wales | KELLOGGS WREXHAM | 338686 | 350344
Dee Valley & Mid Wales | KING GEORGE STREET | 330320 | 368439
Dee Valley & Mid Wales | KINNERLEY | 333287 | 321184
Dee Valley & Mid Wales | KINNERTON | 334804 | 362541
Dee Valley & Mid Wales | LEGACY | 329107 | 347927
Dee Valley & Mid Wales | LIVERPOOL ROAD 33kV | 353621 | 340968
Dee Valley & Mid Wales | LLANARMON | 318585 | 356301
Dee Valley & Mid Wales | LLANDDU QUARRY | 325557 | 322950
Dee Valley & Mid Wales | LLANDINAM | 301836 | 286232
Dee Valley & Mid Wales | LLANDRINIO | 328345 | 317430
Dee Valley & Mid Wales | LLANFAIR CAEREINION | 311159 | 306113
Dee Valley & Mid Wales | LLANFYLLIN | 316261 | 318483
Dee Valley & Mid Wales | LLANGOLLEN | 322035 | 341553
Dee Valley & Mid Wales | LLANIDLOES | 295753 | 285286
Dee Valley & Mid Wales | LLANILAR | 260727 | 275664
Dee Valley & Mid Wales | LLANSANTFRAID | 323355 | 321137
Dee Valley & Mid Wales | LLANSILIN | 321408 | 328690
Dee Valley & Mid Wales | LLAY | 332704 | 356347
Dee Valley & Mid Wales | LLYNCLYS | 328464 | 323966
Dee Valley & Mid Wales | MACHYNLLETH | 275967 | 300793
Dee Valley & Mid Wales | MAELOR CREAMERY | 338630 | 346682
Dee Valley & Mid Wales | MAES Y CLAWDD | 330427 | 327993
Dee Valley & Mid Wales | MAESBURY ROAD | 329771 | 328640
Dee Valley & Mid Wales | MARCHWIEL | 338660 | 349850
Dee Valley & Mid Wales | MILFORD | 309386 | 290491
Dee Valley & Mid Wales | MILL STREET | 258329 | 281405
Dee Valley & Mid Wales | MIXALLOY | 333637 | 364686
Dee Valley & Mid Wales | MMB ELLESMERE | 339921 | 334491
Dee Valley & Mid Wales | MOCHDRE | 309553 | 290111
Dee Valley & Mid Wales | MOLD OFF NEW STREET | 323714 | 363655
Dee Valley & Mid Wales | MONSANTO | 327446 | 342256
Dee Valley & Mid Wales | MORDA | 329068 | 328338
Dee Valley & Mid Wales | MSL DUFFRYN | 328481 | 183692
Dee Valley & Mid Wales | MYNYDD GORDDU | 266298 | 287184
Dee Valley & Mid Wales | NEWTOWN GRID | 312061 | 291800
Dee Valley & Mid Wales | NORTH ROAD | 258666 | 281902
Dee Valley & Mid Wales | NORTH WALES PAPER | 326188 | 371571
Dee Valley & Mid Wales | NORTHOP 33 | 325480 | 368136
Dee Valley & Mid Wales | NWW LLANFORDA | 327621 | 329387
Dee Valley & Mid Wales | OSWESTRY GRID | 330283 | 330548
Dee Valley & Mid Wales | OVERTON | 338738 | 340586
Dee Valley & Mid Wales | PANDY | 333704 | 353400
Dee Valley & Mid Wales | PARC-Y-LLYN 33 | 259445 | 280848
Dee Valley & Mid Wales | PILKINGTONS Q FERRY | 332478 | 367807
Dee Valley & Mid Wales | PONTERWYL | 324100 | 364020
Dee Valley & Mid Wales | PREES | 354766 | 333550
Dee Valley & Mid Wales | QUEENSFERRY | 332325 | 367988
Dee Valley & Mid Wales | RAVEN SQUARE | 321472 | 307402
Dee Valley & Mid Wales | RECSAM COMPONENTS | 337545 | 350144
Dee Valley & Mid Wales | RHOSDDU ROAD | 332973 | 351890
Dee Valley & Mid Wales | RHOSNESNI | 334735 | 351676
Dee Valley & Mid Wales | RHYD BROUGHTON LANE | 332123 | 350736
Dee Valley & Mid Wales | RHYD Y GOLEU | 323135 | 365117
Dee Valley & Mid Wales | RHYDLYDAN | 272357 | 281081
Dee Valley & Mid Wales | RIVERSIDE TERRACE | 258387 | 281365
Dee Valley & Mid Wales | ROSSETT | 336709 | 356911
Dee Valley & Mid Wales | RUABON | 329110 | 343785
Dee Valley & Mid Wales | SANDYCROFT CHES.RD | 333347 | 366627
Dee Valley & Mid Wales | SHAWBURY | 354318 | 322667
Dee Valley & Mid Wales | SYNTHITE | 323219 | 364948
Dee Valley & Mid Wales | TETRA PAK | 337609 | 348291
Dee Valley & Mid Wales | TREGYNON | 310053 | 299169
Dee Valley & Mid Wales | TRYWERYN | 288125 | 340394
Dee Valley & Mid Wales | TUTTLE STREET | 333601 | 350055
Dee Valley & Mid Wales | TYWYN | 259166 | 300895
Dee Valley & Mid Wales | U C WALES | 259927 | 281515
Dee Valley & Mid Wales | W I E CENTRAL | 338038 | 350101
Dee Valley & Mid Wales | WELSHPOOL | 324108 | 306776
Dee Valley & Mid Wales | WEM | 350373 | 329139
Dee Valley & Mid Wales | WEM EAST | 352364 | 329542
Dee Valley & Mid Wales | WEST FELTON | 334463 | 326344
Dee Valley & Mid Wales | WHITCHURCH | 352594 | 342824
Dee Valley & Mid Wales | WHITEGATE | 334953 | 349653
Dee Valley & Mid Wales | WIMPEYS PANT QUARRY | 319841 | 370482
Dee Valley & Mid Wales | WOODFIELD AVENUE | 324746 | 372577
Dee Valley & Mid Wales | WREXHAM | 335134 | 349122
Dee Valley & Mid Wales | YOCKINGS GATE | 354727 | 341985
Merseyside | A C DELCO | 342557 | 397721
Merseyside | ABBOTSFIELD | 353382 | 392380
Merseyside | ACORN FIELD ROAD | 343609 | 398491
Merseyside | AIGBURTH VALE | 337919 | 386826
Merseyside | AINSDALE | 331583 | 412324
Merseyside | AINSWORTH LANE | 342719 | 396487
Merseyside | AINTREE | 336740 | 398306
Merseyside | AINTREE GRID | 337151 | 399706
Merseyside | AIRPORT | 343156 | 382850
Merseyside | ALBERT DOCK | 334213 | 389639
Merseyside | ALDERWOOD AVE | 345265 | 383249
Merseyside | ALEXANDRA PARK | 349991 | 394649
Merseyside | ALLERTON | 340093 | 386513
Merseyside | ALMATEX | 353036 | 394685
Merseyside | ALMONDS TURN | 334639 | 399862
Merseyside | ALTMOUTH | 329538 | 404450
Merseyside | APPLETON | 351691 | 386316
Merseyside | ARUNDEL | 338361 | 388396
Merseyside | ATHOL STREET | 334437 | 392406
Merseyside | ATLANTIC COMPLEX | 335323 | 398215
Merseyside | AXIS BUSINESS PARK | 340156 | 397144
Merseyside | B.R.BANKHALL | 334558 | 393702
Merseyside | BANASTRE ROAD | 333521 | 416040
Merseyside | BATH STREET REACTOR | 333765 | 390819
Merseyside | BEAUMARIS STREET | 334079 | 393777
Merseyside | BEAUMONT STREET | 336899 | 389370
Merseyside | BEDBURN DRIVE | 342590 | 391199
Merseyside | BEECH STREET | 337448 | 390809
Merseyside | BEMROSE | 337294 | 395937
Merseyside | BIBBYS | 333575 | 394403
Merseyside | BICC HUYTON QUARRY | 345442 | 390488
Merseyside | BIXTETH STREET | 334146 | 390760
Merseyside | BLUEBELL LANE | 344063 | 391855
Merseyside | BLUNDELL STREET | 334796 | 389413
Merseyside | BLUNDELLSANDS NORTH | 330696 | 400140
Merseyside | BLUNDELLSANDS SOUTH | 331013 | 399625
Merseyside | BOLTON STREET | 335094 | 390374
Merseyside | BOODECROFT | 342723 | 394003
Merseyside | BOOTLE | 334644 | 395956
Merseyside | BRECKFIELD 33KV | 336168 | 392337
Merseyside | BRITAIN OILS | 334035 | 393499
Merseyside | BRITISH OXYGEN | 351362 | 397225
Merseyside | BRITISH SIDAC | 352951 | 393797
Merseyside | BROADGREEN | 340838 | 390182
Merseyside | BROOK BRIDGE | 345730 | 392621
Merseyside | BROOK STREET | 333843 | 390822
Merseyside | BUCKINGHAM STREET | 335145 | 392274
Merseyside | BURLINGTON AVENUE | 330736 | 407134
Merseyside | BURLINGTON STREET | 334028 | 391721
Merseyside | BURTONHEAD ROAD | 350879 | 394616
Merseyside | BURTONWOOD | 356419 | 392949
Merseyside | CABLE STREET | 334524 | 390234
Merseyside | CABLE STREET B | 334505 | 390244
Merseyside | CALDWELL RD MOSTYN | 340561 | 385554
Merseyside | CAMBRIDGE ROAD | 335167 | 418257
Merseyside | CARBORUNDUM | 348988 | 399362
Merseyside | CARLTON STREET | 350196 | 395244
Merseyside | CARNEGIE ROAD | 338402 | 391816
Merseyside | CARR LANE 33 | 332788 | 413334
Merseyside | CARR LANE EAST | 339763 | 394864
Merseyside | CARR LANE ROBY | 343222 | 390527
Merseyside | CEW | 352086 | 396210
Merseyside | CHALON WAY | 351415 | 395151
Merseyside | CHILDERS STREET | 339012 | 391171
Merseyside | CHILDWALL | 341355 | 388234
Merseyside | CHILDWALL FIVEWAYS | 340365 | 389359
Merseyside | CHILDWALL VALLEY RD | 342995 | 388744
Merseyside | CHIRON SHAW ROAD | 343771 | 384140
Merseyside | CHISENHALE STREET | 334065 | 391505
Merseyside | CLOCKFACE | 353441 | 391545
Merseyside | CLUBMOOR | 337807 | 393449
Merseyside | CONIX | 344062 | 384037
Merseyside | CRONTON | 347787 | 389505
Merseyside | CROPPER STREET | 335022 | 390207
Merseyside | CROSBY | 332880 | 400318
Merseyside | CROWN COURTS | 334328 | 390198
Merseyside | CROXTETH | 341258 | 393517
Merseyside | CROXTETH COUNTRY PK | 341666 | 395208
Merseyside | DAILY POST AND ECHO | 333864 | 390702
Merseyside | DANS ROAD WIDNES | 353315 | 386790
Merseyside | DELAMORE STREET | 335246 | 394346
Merseyside | DELTA METALS | 353303 | 395668
Merseyside | DESOTO ROAD | 350452 | 384329
Merseyside | DEYES LANE | 338875 | 402561
Merseyside | DICKINSONS | 342713 | 398255
Merseyside | DINGLE | 336393 | 387927
Merseyside | DINGLE VALE | 336071 | 387190
Merseyside | DISTA PRODUCTS | 343485 | 384689
Merseyside | DITTON | 349767 | 386326
Merseyside | DODDS LANE | 337883 | 402886
Merseyside | DONALDSON STREET | 336273 | 392918
Merseyside | DOVER ROAD | 332536 | 414693
Merseyside | DUNLOPS WALTON | 336167 | 395519
Merseyside | EAST PRESCOT ROAD | 342142 | 391892
Merseyside | ECCLESTON | 347352 | 393313
Merseyside | ECP WEST-BANKS RD | 341307 | 383518
Merseyside | EDGE HILL | 336496 | 390160
Merseyside | EDGE LN TAPLEY | 338922 | 390717
Merseyside | ELBOW LANE | 329765 | 407140
Merseyside | ELEPHANT LANE HOTEL | 349844 | 393438
Merseyside | ESTUARY COMMERCE PK | 342084 | 383534
Merseyside | EVERTON BROW | 335334 | 391425
Merseyside | EVERTON ROAD | 335842 | 391612
Merseyside | FAZAKERLEY | 337524 | 396428
Merseyside | FAZAKERLEY HOSPITAL | 338231 | 397174
Merseyside | FORDS (HALEWOOD) | 344821 | 384430
Merseyside | FORMBY | 330976 | 406964
Merseyside | FRESHFIELD | 329076 | 408368
Merseyside | GARDNER RD TUEBROOK | 338414 | 392443
Merseyside | GARDNERS ROW | 334730 | 391378
Merseyside | GARSTON | 340525 | 384460
Merseyside | GATEACRE | 344167 | 388759
Merseyside | GAVIN ROAD | 348637 | 385453
Merseyside | GEC ST HELENS | 350829 | 391324
Merseyside | GILLMOSS | 340482 | 396569
Merseyside | GIRO BOOTLE | 335615 | 397686
Merseyside | GLOVERS BROW | 340303 | 399301
Merseyside | GRADWELL STREET | 334714 | 390023
Merseyside | GRANBY | 335715 | 389120
Merseyside | GRANOX | 350346 | 384067
Merseyside | GRANTHAM CLOSE | 333152 | 414141
Merseyside | GREEK STREET | 335411 | 390587
Merseyside | GROVE PARK | 337240 | 388545
Merseyside | H P O COPPERAS HILL | 335226 | 390375
Merseyside | HALEWOOD | 344911 | 384424
Merseyside | HALEWOOD ROAD | 343177 | 387215
Merseyside | HAMMOND ROAD | 343449 | 399442
Merseyside | HAREFIELD ROAD | 343879 | 383147
Merseyside | HARRINGTON STREET A | 334470 | 390364
Merseyside | HARRINGTON STREET B | 334470 | 390353
Merseyside | HASKAYNE | 335948 | 407514
Merseyside | HATTONS LANE | 340257 | 388628
Merseyside | HIGHFIELD STREET A | 334313 | 390834
Merseyside | HIGHFIELD STREET B | 334314 | 390833
Merseyside | HILLS MOSS | 354032 | 393008
Merseyside | HOLBORN HILL | 340021 | 407003
Merseyside | HOLT LANE WARR RD | 348270 | 391852
Merseyside | HORNHOUSE LANE | 342972 | 397639
Merseyside | HORNSBRIDGE | 352452 | 387845
Merseyside | HOUGH GREEN | 348521 | 387203
Merseyside | HOUGHTONS LANE | 348062 | 396261
Merseyside | HSE PEMBROKE ROAD | 334222 | 394894
Merseyside | HUNTS CROSS | 343610 | 385935
Merseyside | HUYTON | 342918 | 392176
Merseyside | HUYTON HEY ROAD | 344617 | 390700
Merseyside | HY TEN BRIDLE ROAD | 335864 | 397595
Merseyside | INLAND REVENUE | 334576 | 394916
Merseyside | IVY AVENUE | 339495 | 385329
Merseyside | IVY STREET | 334858 | 416705
Merseyside | JACOBS | 337031 | 396250
Merseyside | KELCO | 343066 | 396781
Merseyside | KELLOGGS | 332842 | 396465
Merseyside | KEMPSTON | 335316 | 390798
Merseyside | KENSINGTON RD 33 | 334412 | 416905
Merseyside | KENTON ROAD | 344982 | 385240
Merseyside | KERSHAW AVENUE | 332702 | 399200
Merseyside | KINGS COURT | 332907 | 397483
Merseyside | KINGS DOCK | 334348 | 389279
Merseyside | KINGSWAY TUNNEL | 333709 | 391425
Merseyside | KIRKBY | 343649 | 397314
Merseyside | KIRKBY CENTRAL | 341252 | 398777
Merseyside | KIRKDALE | 335493 | 392958
Merseyside | KIRKSTONE ROAD WEST | 333510 | 398780
Merseyside | KNOTTY ASH | 340650 | 391688
Merseyside | KNOWSLEY | 343758 | 395362
Merseyside | KODAK | 343760 | 398960
Merseyside | LARK LANE | 337278 | 387620
Merseyside | LEA GREEN | 350817 | 392162
Merseyside | LEEWARD DRIVE | 342201 | 383936
Merseyside | LEYFIELD ROAD | 340580 | 392666
Merseyside | LICKERS LANE HOUSING | 347554 | 390646
Merseyside | LIME STREET | 334916 | 390485
Merseyside | LISTER DRIVE | 338156 | 391821
Merseyside | LISTER DRIVE 6KV | 338143 | 391817
Merseyside | LITHERLAND | 333045 | 398081
Merseyside | LITTLEWOODS | 333970 | 390929
Merseyside | LIVERPOOL INT BUS PARK | 341331 | 383511
Merseyside | LIVERPOOL UNIVERSITY | 336117 | 390272
Merseyside | LONGVIEW | 344751 | 391562
Merseyside | LORD STREET | 334093 | 417610
Merseyside | LOUDON GROVE | 336311 | 388723
Merseyside | LOWER LANE | 338992 | 395842
Merseyside | LUCAS FAZAKERLEY | 337586 | 395684
Merseyside | LUCAS HUYTON | 346064 | 389708
Merseyside | LUGSDALE | 351944 | 385718
Merseyside | LYNDENE ROAD | 342167 | 388949
Merseyside | MAGHULL | 337527 | 401571
Merseyside | MANN ISLAND | 334049 | 390017
Merseyside | MARKET STREET | 333585 | 417051
Merseyside | MARLED HEY | 342095 | 393667
Merseyside | MARSH BROWS | 329196 | 406981
Merseyside | MARSHALL CROSS BRIDGE | 351902 | 392400
Merseyside | MARSHSIDE | 335724 | 419160
Merseyside | MASEFIELD ROAD | 334163 | 400566
Merseyside | MATHER AVENUE | 339789 | 387497
Merseyside | MDHB BRUNSWICK DOCK | 334792 | 388613
Merseyside | MDHB CANADA DOCK | 333716 | 393749
Merseyside | MDHB FREEPORT | 332412 | 397094
Merseyside | MDHB HUSKISSON DK | 333659 | 393215
Merseyside | MEDEVA | 343777 | 383953
Merseyside | MEDIMMUNE | 343940 | 384096
Merseyside | MERSEY BRIDGE | 350927 | 384902
Merseyside | METAL BOX | 343184 | 383964
Merseyside | MIDDLEMASS HEY | 344308 | 388205
Merseyside | MIDLAND BANK | 335819 | 397686
Merseyside | MILL LN WAVERTREE | 339252 | 389571
Merseyside | MILL STREET | 350879 | 395738
Merseyside | MOOR LANE BY PASS | 332142 | 399925
Merseyside | MOSS LANE | 334252 | 397936
Merseyside | MOSSLEY HILL | 338816 | 386859
Merseyside | MUIRHEAD AV-OGDEN CL | 339116 | 393549
Merseyside | MULLARDS BALMORAL DR | 337068 | 419327
Merseyside | N C B SUTTON MANOR | 351701 | 390664
Merseyside | NAYLORS ROAD | 343634 | 388529
Merseyside | NELSON STREET BOOTLE | 333510 | 394720
Merseyside | NETHERTON | 335797 | 399955
Merseyside | NEVILL STREET | 333429 | 417531
Merseyside | NEW BOLD | 354040 | 393024
Merseyside | NEW BROADGREEN HOSPITAL | 340183 | 390797
Merseyside | NEWS INTERNATIONAL | 343334 | 396827
Merseyside | NORRIS GREEN | 338272 | 394438
Merseyside | NORTH JOHNS STREET | 350859 | 395469
Merseyside | NORTH SEAFORTH | 332089 | 397353
Merseyside | NORTHWAY MAGHULL | 337220 | 400759
Merseyside | NORTHWOOD | 342034 | 398975
Merseyside | NORTON SCRAP | 333804 | 393672
Merseyside | NWW SHELL GREEN | 353349 | 386142
Merseyside | NWWA SANDON DOCK | 333746 | 392835
Merseyside | OCEAN PLAZA | 333197 | 417937
Merseyside | OLD HAYMARKET, PALE STREET | 334732 | 390753
Merseyside | OLD ROAN | 337076 | 399172
Merseyside | OLDHAM PLACE | 335306 | 390044
Merseyside | ORB CLOSE | 340433 | 395511
Merseyside | ORRELL MOUNT | 334172 | 397032
Merseyside | OTIS ELEVATOR | 342204 | 397189
Merseyside | P B WATSON STREET | 350923 | 394668
Merseyside | PACIFIC ROAD | 333630 | 395440
Merseyside | PADDINGTON PLACE | 336327 | 390293
Merseyside | PALCO | 342270 | 396544
Merseyside | PALL MALL PRIMARY | 334136 | 390858
Merseyside | PARADISE STREET | 334588 | 389912
Merseyside | PEETS LANE | 336322 | 418289
Merseyside | PETER SPENCE | 352672 | 387750
Merseyside | PHYTHIAN STREET | 336223 | 391097
Merseyside | PILK GREENGATE WKS | 351051 | 394529
Merseyside | PILK SULLIVAN | 352682 | 385202
Merseyside | PILKINGTON DAM ROW | 350425 | 394483
Merseyside | PILKINGTON HO | 349970 | 394523
Merseyside | PILKINGTONS PLATE | 350952 | 396915
Merseyside | PINFOLD LANE | 331267 | 411127
Merseyside | PITT STREET | 351217 | 384504
Merseyside | PLESSEY EDGE LANE | 338247 | 390757
Merseyside | PONTINS | 330132 | 412681
Merseyside | POULTON ROAD | 335607 | 417245
Merseyside | PRESCOT | 346798 | 392064
Merseyside | RAINFORD | 347948 | 400532
Merseyside | RAINHILL LOCAL | 349720 | 390913
Merseyside | RAVENHEAD GRID | 350866 | 394603
Merseyside | RAVENHEAD RETAIL PARK | 351155 | 394615
Merseyside | RAVENSMEOLS LANE | 330120 | 406492
Merseyside | REGENT ROAD | 333807 | 393662
Merseyside | RIGBY STREET PRIMARY | 334033 | 390910
Merseyside | ROBBINS BRIDGE | 338570 | 404264
Merseyside | ROPEWALKS | 334872 | 389781
Merseyside | ROYAL INS | 333892 | 390585
Merseyside | ROYAL LIVERPOOL HOSPITAL | 336054 | 390829
Merseyside | RTZ | 348557 | 385193
Merseyside | SANDFIELD ROAD | 342699 | 387619
Merseyside | SANDHILLS LANE | 334174 | 393102
Merseyside | SCARISBRICK AVENUE | 333700 | 397181
Merseyside | SEAFORTH | 333065 | 396371
Merseyside | SEEDS LANE | 337419 | 397272
Merseyside | SESSIONS ROAD | 335016 | 393585
Merseyside | SHEIL PARK | 337104 | 391975
Merseyside | SHEPPARDS ALEX DOCKS | 333391 | 394898
Merseyside | SHERDLEY ROAD | 351819 | 394255
Merseyside | SHEVINGTONS LANE | 341630 | 400438
Merseyside | SIMONSWOOD | 342978 | 399713
Merseyside | SLAIDBURN CRESCENT | 336445 | 419958
Merseyside | SOMERFIELD DISTRIBUTION | 351007 | 392102
Merseyside | SONAE | 342767 | 399274
Merseyside | SOUTHDENE | 341769 | 397560
Merseyside | SOUTHPORT | 336510 | 416761
Merseyside | SOUTHPORT RD LYDIATE | 337269 | 403243
Merseyside | SOUTHPORT ROAD | 330551 | 408447
Merseyside | SPEKE | 343573 | 384304
Merseyside | SPEKE HALL ROAD | 342510 | 384700
Merseyside | SPEKE SKY PARK | 342856 | 383051
Merseyside | ST HELENS | 349826 | 395335
Merseyside | ST HELENS LINKWAY | 351892 | 394482
Merseyside | ST HELENS WWTW | 353568 | 395775
Merseyside | ST IVEL FOODS | 342114 | 397086
Merseyside | ST JAMES | 334953 | 388977
Merseyside | STANLEY PARK | 336604 | 393430
Merseyside | STH.MOSSLEY HILL RD. | 339391 | 386138
Merseyside | STONEBRIDGE LANE | 339595 | 396225
Merseyside | STONEYCROFT | 339394 | 392122
Merseyside | STRAND GATE BOOTLE | 333137 | 395551
Merseyside | SUBURBAN ROAD | 337083 | 392708
Merseyside | SUTTON HEATH | 350811 | 393231
Merseyside | TARBOCK | 346227 | 390101
Merseyside | TATTON ROAD | 335942 | 396845
Merseyside | TECHNOLOGY CAMPUS | 351881 | 395731
Merseyside | THATTO HEATH ROAD | 349575 | 393994
Merseyside | THINGWALL | 341125 | 390993
Merseyside | TOWER HILL | 341020 | 399810
Merseyside | TRAFALGAR DOCK | 333639 | 391525
Merseyside | TREATMENT WORKS | 333754 | 392850
Merseyside | TUDOR ROAD | 330869 | 412462
Merseyside | UPTON ROCKS 33 | 349981 | 387096
Merseyside | USAC | 352752 | 385818
Merseyside | VIOLET STREET | 351096 | 385126
Merseyside | WALTON | 335788 | 394921
Merseyside | WALTON TRIANGLE | 337204 | 395513
Merseyside | WANGO LANE | 338861 | 398207
Merseyside | WAPPING | 334459 | 389169
Merseyside | WARD BLENKINSOP | 346993 | 384867
Merseyside | WASHINGTON STREET | 334078 | 395565
Merseyside | WATERLOO | 331854 | 398145
Merseyside | WATERPARK DRIVE | 342839 | 393176
Merseyside | WATERY LANE | 353550 | 394126
Merseyside | WAVERTREE | 339018 | 388483
Merseyside | WAVERTREE BOULEVARD | 337693 | 390261
Merseyside | WAVERTREE VALE | 337981 | 389512
Merseyside | WEAVER IND EST | 340186 | 383656
Merseyside | WELLFIELD AVENUE | 341833 | 398158
Merseyside | WEST DERBY | 339511 | 392852
Merseyside | WEST VALE | 340482 | 398458
Merseyside | WESTSIDE | 342469 | 384207
Merseyside | WHISTON | 346769 | 390803
Merseyside | WHISTON HOSPITAL | 348155 | 391815
Merseyside | WIDNES | 350752 | 385204
Merseyside | WIDNES BIOMASS | 350032 | 384425
Merseyside | WIDNES ROAD | 356038 | 387551
Merseyside | WILSON ROAD | 345313 | 390203
Merseyside | WINDLE 33kV | 350970 | 397004
Merseyside | WINDLEHURST | 350263 | 396672
Merseyside | WINSLADE ROAD | 336803 | 394548
Merseyside | WOOD LANE | 344931 | 387608
Merseyside | WOODEND AVENUE | 343313 | 384464
Merseyside | WOODVILLE STREET | 351652 | 395779
Merseyside | WOOLTON | 342611 | 386722
Merseyside | YEWTREE ROAD | 340614 | 387022
Merseyside | YORK ROAD | 332814 | 415818
Merseyside | YORKSHIRE IMPERIAL METALS | 343389 | 397120
Mid Cheshire | ACER AVENUE | 371060 | 357134
Mid Cheshire | ACTON | 363081 | 353444
Mid Cheshire | ANDERTON | 364888 | 375729
Mid Cheshire | ARPLEY LANDFILL GEN | 359024 | 386869
Mid Cheshire | AUDLEM | 367283 | 344400
Mid Cheshire | B RLY STEELWORKS | 369391 | 355895
Mid Cheshire | BAE RADWAY | 377824 | 354346
Mid Cheshire | BARBAULD STREET | 360656 | 387877
Mid Cheshire | BASFORD SIDINGS | 370838 | 352754
Mid Cheshire | BATTERSBY LANE | 361223 | 388960
Mid Cheshire | BEWSEY | 359296 | 389073
Mid Cheshire | BOULEVARD | 359197 | 391319
Mid Cheshire | BOWMAKERS | 367106 | 366736
Mid Cheshire | BR STATION | 370867 | 354992
Mid Cheshire | BRINDLEY | 359473 | 354082
Mid Cheshire | BRITISH ALUMINIUM LATCHFRD | 363749 | 387463
Mid Cheshire | CASTLE BEESTON ST | 365353 | 373318
Mid Cheshire | CHAPELFORD | 357188 | 389306
Mid Cheshire | CHESHIRE GREEN | 360117 | 357505
Mid Cheshire | CHESTER ROAD | 360342 | 386456
Mid Cheshire | CHURCH LAWTON | 381705 | 355650
Mid Cheshire | CHURCH ST WINSFORD | 365375 | 366450
Mid Cheshire | CINNAMON 33 | 363098 | 391626
Mid Cheshire | CIVIC CENTRE | 370751 | 355641
Mid Cheshire | CLAUGHTON AVENUE | 370450 | 354077
Mid Cheshire | CLEDFORD | 370858 | 364468
Mid Cheshire | COMBERMERE ABBEY | 360334 | 344776
Mid Cheshire | COPPENHALL | 371602 | 356648
Mid Cheshire | CREWE GRID A | 367596 | 356395
Mid Cheshire | CREWE GRID B | 367634 | 356356
Mid Cheshire | CROMWELL AVENUE 33 | 358364 | 390944
Mid Cheshire | CROSSFIELDS | 359892 | 388134
Mid Cheshire | CROWTON | 357914 | 373998
Mid Cheshire | DALLAM GRID | 360176 | 390722
Mid Cheshire | DARNHALL | 364667 | 364934
Mid Cheshire | DUCHY ROAD | 372381 | 353936
Mid Cheshire | DUCKINGTON | 349596 | 351787
Mid Cheshire | EDEN VALE | 360188 | 372383
Mid Cheshire | ELECTRA WAY | 372039 | 354930
Mid Cheshire | ELECTRICITY STREET | 370469 | 355313
Mid Cheshire | ELWORTH 33 | 373018 | 362995
Mid Cheshire | ERF WAY | 371751 | 365618
Mid Cheshire | FISONS | 376720 | 366752
Mid Cheshire | FODENS | 373925 | 360988
Mid Cheshire | GADBROOK | 367940 | 372443
Mid Cheshire | GATEWARTH SEWAGE | 358251 | 387265
Mid Cheshire | GIGG LANE THELWALL | 365174 | 387455
Mid Cheshire | GRAPPENHALL | 364082 | 387364
Mid Cheshire | GRAVEL | 367396 | 366275
Mid Cheshire | GREAT SANKEY | 357987 | 387830
Mid Cheshire | GREENALL WHITLEY | 361245 | 386779
Mid Cheshire | GRIFFITHS ROAD | 368151 | 373962
Mid Cheshire | HARTFORD | 363358 | 371369
Mid Cheshire | HASLINGTON | 373509 | 356890
Mid Cheshire | HATHERTON | 368026 | 347273
Mid Cheshire | HAWLEYS LANE | 360468 | 390300
Mid Cheshire | HILLCLIFFE | 361636 | 384898
Mid Cheshire | HOLE HOUSE FARM | 369500 | 360250
Mid Cheshire | HOLMES CHAPEL | 376549 | 367733
Mid Cheshire | HOOD MANOR | 358306 | 388834
Mid Cheshire | HORROCKS LANE | 360756 | 388215
Mid Cheshire | I.C.I.LOSTOCK | 368406 | 373874
Mid Cheshire | ILFORDS | 378012 | 380210
Mid Cheshire | IVECO | 366838 | 367208
Mid Cheshire | KINGSLAND 33 | 364475 | 390400
Mid Cheshire | KINGSWAY NORTH | 362458 | 388995
Mid Cheshire | KNUTSFORD GRID | 375234 | 377923
Mid Cheshire | LATCHFORD | 362841 | 387393
Mid Cheshire | LEICESTER STREET | 366004 | 374293
Mid Cheshire | LEIGHTON HOSPITAL | 368156 | 357794
Mid Cheshire | LEVERS CROSSFIELD | 359887 | 388124
Mid Cheshire | LONGBARN LANE | 364474 | 390400
Mid Cheshire | LOSTOCK GRID | 369205 | 374498
Mid Cheshire | LOSTOCK TRIANGLE | 369402 | 374962
Mid Cheshire | LYMM | 367330 | 387167
Mid Cheshire | MERE | 372865 | 381450
Mid Cheshire | MIDDLEWICH | 371661 | 366740
Mid Cheshire | MIDLAND ROLLMAKERS | 371379 | 354172
Mid Cheshire | MIDPOINT POCHIN WAY | 371679 | 365563
Mid Cheshire | MILNER 33 | 359753 | 388180
Mid Cheshire | MOBBERLEY | 377768 | 379897
Mid Cheshire | MORRISONS | 368532 | 372532
Mid Cheshire | NANTWICH | 365733 | 352368
Mid Cheshire | NEWHALL | 360504 | 344936
Mid Cheshire | NORTH WEST FARMERS | 359989 | 357672
Mid Cheshire | NORTH WESTERN MILLS | 370714 | 353723
Mid Cheshire | NORTHWICH TOWN | 365943 | 374075
Mid Cheshire | NWW CAMPUS | 355956 | 390068
Mid Cheshire | OMEGA | 357217 | 390409
Mid Cheshire | ORFORD | 361987 | 390635
Mid Cheshire | ORFORD ROAD | 361989 | 389896
Mid Cheshire | ORION BOULEVARD | 356004 | 390272
Mid Cheshire | OVER | 364194 | 366156
Mid Cheshire | OWEN STREET | 360357 | 389134
Mid Cheshire | PADGATE | 363082 | 389965
Mid Cheshire | PARR STREET | 361177 | 387953
Mid Cheshire | PENKETH | 356546 | 388132
Mid Cheshire | PLUMLEY | 372033 | 374994
Mid Cheshire | PRIMROSE HALL | 374906 | 366791
Mid Cheshire | RADBROKE HALL | 376928 | 374681
Mid Cheshire | RADWAY GREEN | 377556 | 354152
Mid Cheshire | RHM FOODS LTD | 371935 | 364348
Mid Cheshire | RINGWAY | 380010 | 385342
Mid Cheshire | RODNEY STREET | 360714 | 388845
Mid Cheshire | ROLLS ROYCE | 368662 | 356607
Mid Cheshire | RYLANDS ELDON ST | 361251 | 388463
Mid Cheshire | SAFEWAY | 365410 | 389573
Mid Cheshire | SANDBACH | 375545 | 361971
Mid Cheshire | SANKEY BRIDGES | 358612 | 387465
Mid Cheshire | SCHOLAR GREEN | 383204 | 357610
Mid Cheshire | SLUTCHERS LANE GEN | 360214 | 387497
Mid Cheshire | SMALLWOOD | 381854 | 360839
Mid Cheshire | SNOWHILL | 365010 | 352474
Mid Cheshire | SOLVAY INTEROX | 359883 | 386176
Mid Cheshire | STAPELEY | 367537 | 351151
Mid Cheshire | STIRLING CABLES | 360339 | 388698
Mid Cheshire | STOCKTON HEATH | 361379 | 386134
Mid Cheshire | TACO PLASTICS | 366924 | 367166
Mid Cheshire | THAMES BOARD MILL | 360283 | 386752
Mid Cheshire | THELWALL | 365416 | 387796
Mid Cheshire | THELWALL LANE GEN | 363965 | 387445
Mid Cheshire | TRICKETTS LANE | 368128 | 352374
Mid Cheshire | TWYFORDS | 380983 | 355300
Mid Cheshire | UNITED GAS STORAGE | 369495 | 360370
Mid Cheshire | UNITED PERIPHERALS | 366660 | 367425
Mid Cheshire | WARRINGTON 33kV | 362258 | 388093
Mid Cheshire | WARRINGTON CENTRAL | 360507 | 388387
Mid Cheshire | WCB PLASTICS | 367106 | 366599
Mid Cheshire | WELL LANE WEAVERHAM | 361126 | 374812
Mid Cheshire | WESTBROOK | 358189 | 390216
Mid Cheshire | WESTON | 373551 | 352961
Mid Cheshire | WHARTON | 367034 | 366925
Mid Cheshire | WHARTON PARK | 365698 | 367185
Mid Cheshire | WHEELOCK | 375477 | 359677
Mid Cheshire | WHITELEGGS LANE | 369580 | 386257
Mid Cheshire | WHITTLE BROOK 33 | 357220 | 390160
Mid Cheshire | WINCHAM | 367725 | 375411
Mid Cheshire | WINNINGTON | 363986 | 374171
Mid Cheshire | WINSFORD | 367078 | 366943
Mid Cheshire | WINSFORD SALT | 366399 | 368745
Mid Cheshire | WINWICK QUAY | 360287 | 391423
Mid Cheshire | WISTASTON HALL | 368515 | 354216
Mid Cheshire | WOODFORD PARK | 362972 | 365356
Mid Cheshire | WOOLSTON | 364163 | 389602
Mid Cheshire | WRENBURY FRITH | 357441 | 348640
North Wales | ABERGELE | 296002 | 376524
North Wales | ABERSOCH | 230004 | 327907
North Wales | ALPOCO | 227064 | 380605
North Wales | AMLWCH | 244715 | 393003
North Wales | BANGOR 33kV | 254513 | 370274
North Wales | BANGOR HOSPITAL | 256001 | 370262
North Wales | BANGOR UNIVERSITY | 257103 | 371860
North Wales | BEAUMARIS | 258543 | 377747
North Wales | BENLECH 33KV | 251372 | 382937
North Wales | BETHESDA | 261740 | 366219
North Wales | BETWS-Y-COED | 279458 | 356625
North Wales | BLAENAU FFESTINIOG | 269586 | 345809
North Wales | BOTWNNOG | 226376 | 331054
North Wales | BRENIG | 299923 | 358311
North Wales | BRYN STANLEY | 304656 | 365687
North Wales | BUTLINS | 242933 | 336883
North Wales | CAERGEILIOG | 230459 | 378177
North Wales | CAERNARFON | 249158 | 363544
North Wales | CARMEL | 249399 | 355528
North Wales | CAUSEWAY | 279028 | 377831
North Wales | CEMAES BAY | 236985 | 392777
North Wales | CHURCH LANE | 306588 | 383002
North Wales | CLAWDD NEWYDD | 308876 | 352710
North Wales | CLOCAENOG | 301282 | 358764
North Wales | COLWYN BAY | 282635 | 379195
North Wales | CONWY | 277535 | 377894
North Wales | CWM DYLI | 265324 | 353975
North Wales | DEGANWY | 278810 | 379219
North Wales | DEINIOLEN | 258578 | 362763
North Wales | DENBIGH | 305832 | 366832
North Wales | DOLGARROG | 277037 | 367662
North Wales | DYSERTH ROAD | 303024 | 381241
North Wales | EDERN | 227975 | 338985
North Wales | EGA ELECTRIC | 303225 | 373789
North Wales | EITHINOG | 256461 | 371489
North Wales | FERODO | 249970 | 365497
North Wales | FFERM WYNT RHYDYGROES | 240142 | 392277
North Wales | FFORDD LAS | 301178 | 380649
North Wales | FOUR CROSSES | 239862 | 339783
North Wales | GAERWEN | 248803 | 371086
North Wales | GAERWEN VIEW | 247526 | 371275
North Wales | GANOL STW | 280630 | 377311
North Wales | GLAN CONWY TY DU FM | 280568 | 375481
North Wales | GRAIG FAWR | 305655 | 380159
North Wales | GREENFIELD | 319926 | 377999
North Wales | GWALCHMAI | 238948 | 375450
North Wales | HAMILTON OILS | 312106 | 383899
North Wales | HARBWR | 248173 | 363401
North Wales | HARLECH | 258330 | 331662
North Wales | HIRAEL | 258420 | 372593
North Wales | HOLWAY ROAD | 318129 | 376188
North Wales | HOLYHEAD | 225016 | 381794
North Wales | HOLYWELL | 314647 | 374288
North Wales | IVY STREET | 285024 | 378952
North Wales | LLAINGOCH | 223501 | 382479
North Wales | LLANBEDROG | 231915 | 333069
North Wales | LLANBERIS | 258627 | 359625
North Wales | LLANDDEUSANT | 235600 | 384068
North Wales | LLANDEGFAN | 256140 | 373859
North Wales | LLANDUDNO | 278543 | 381211
North Wales | LLANDUDNO JUNCTION | 280302 | 377903
North Wales | LLANDYFRYDOG | 246396 | 388162
North Wales | LLANDYRNOG | 311204 | 365708
North Wales | LLANERCHYMEDD | 241211 | 384621
North Wales | LLANFAELOG | 234394 | 373118
North Wales | LLANFAIR PG | 253411 | 372441
North Wales | LLANFAIRFECHAN | 268668 | 374354
North Wales | LLANFROTHEN | 261598 | 340245
North Wales | LLANFWROG | 311079 | 357617
North Wales | LLANGAFFO | 244499 | 368126
North Wales | LLANGEFNI | 246049 | 375522
North Wales | LLANGEFNI IND ESTATE | 246255 | 374817
North Wales | LLANGRISTIOLUS 33 | 243622 | 372673
North Wales | LLANLLECHID | 262042 | 369293
North Wales | LLANRWST | 280829 | 361041
North Wales | LLANSANNAN | 294146 | 365819
North Wales | LLYN ALAW | 238508 | 387107
North Wales | LLYSFAEN ROAD | 287375 | 378178
North Wales | LYNWOOD AVENUE RHYL | 301621 | 381597
North Wales | MAENTWROG GRID | 265437 | 339474
North Wales | MANOD | 270462 | 343035
North Wales | MINFFORDD | 257800 | 370928
North Wales | MOEL MAELOGEN | 284530 | 361742
North Wales | MONA | 241847 | 375289
North Wales | MORFA AVE KINMEL BAY | 298411 | 379985
North Wales | NANT HALL | 307704 | 383200
North Wales | NANT-Y-GAMAR | 280112 | 381690
North Wales | OCTEL | 244888 | 393756
North Wales | OLD MILL | 285584 | 378131
North Wales | PARC BRYN CEGIN | 258875 | 370480
North Wales | PARC CYBI | 225624 | 380836
North Wales | PARC MENAI | 254176 | 370052
North Wales | PEBLIC MILLS | 249083 | 361943
North Wales | PENMAENMAWR | 271715 | 375905
North Wales | PENRHYN-SIDE | 281524 | 381702
North Wales | PENSARN | 294672 | 378513
North Wales | PENTRAETH | 250996 | 378502
North Wales | PENYGROES | 245854 | 353545
North Wales | PILKINGTONS | 301875 | 374029
North Wales | POINT OF AYR LOCAL | 312562 | 383472
North Wales | PORTHMADOG | 256638 | 339531
North Wales | PRESTATYN | 306433 | 382913
North Wales | PROMENADE | 300660 | 381656
North Wales | PWLLHELI | 237521 | 335742
North Wales | REFORM STREET | 278192 | 382277
North Wales | RHOS ON SEA | 283534 | 380983
North Wales | RHOSLAN | 248131 | 340747
North Wales | RHUDDLAN | 302174 | 377366
North Wales | RHYD Y FOEL | 291145 | 375780
North Wales | RHYL | 301195 | 380247
North Wales | RIVALS | 238381 | 345666
North Wales | RUTHIN | 313084 | 359132
North Wales | ST ASAPH BUS PARK | 301799 | 374570
North Wales | ST ASAPH GRID | 302087 | 374235
North Wales | ST HELENS ROAD | 248094 | 362038
North Wales | TRYSGLWYN | 244213 | 389282
North Wales | TY-NEWYDD-SPLASH PT | 302177 | 382391
North Wales | UPPER CLYNNOG | 246219 | 346394
North Wales | WAENFAWR | 252789 | 360790
North Wales | WESTBOURNE AVENUE | 300057 | 380736
North Wales | YNNI CYMRU ALF | 302081 | 374245
North Wales | YSBYTY GLAN CLWYD | 300168 | 375954
Wirral | AIR PRODUCTS | 341905 | 375057
Wirral | AMERICAN CAN CO | 356543 | 379630
Wirral | ARROWE PARK HOSPITAL | 327177 | 386630
Wirral | ASSOCIATED LEAD | 341691 | 366694
Wirral | ASTMOOR IND EST | 352972 | 383176
Wirral | B X L BROMBOROUGH | 335124 | 382533
Wirral | BARNSTON | 327137 | 382847
Wirral | BASS CHARRINGTON | 356612 | 379691
Wirral | BEAUFORT ROAD STOR | 330450 | 390052
Wirral | BENTINCK STREET | 331479 | 388724
Wirral | BICC HELSBY | 348296 | 374926
Wirral | BIDSTON | 327938 | 389404
Wirral | BIRKENHEAD CENTRAL | 332144 | 388673
Wirral | BLACON | 337900 | 368580
Wirral | BODFARI PRODUCERS | 338044 | 362318
Wirral | BOOSTON WOOD | 338171 | 379090
Wirral | BOWATERS CONTAINERS | 339183 | 378209
Wirral | BR SHORE ROAD | 332781 | 389217
Wirral | BRIDGE STREET | 337837 | 365037
Wirral | BRITISH GYPSUM | 356704 | 379658
Wirral | BRITISH PIPE ASS | 341924 | 374546
Wirral | BRITISH RAIL BROMBGH | 334388 | 380923
Wirral | BROMBOROUGH | 335892 | 382355
Wirral | BROOK LANE | 340708 | 367446
Wirral | BUILDWAS ROAD | 329392 | 378674
Wirral | BURMAH OIL | 342387 | 375979
Wirral | CADBURYS | 326278 | 390905
Wirral | CALDY | 322683 | 385184
Wirral | CALDY VALLEY ROAD | 342592 | 365163
Wirral | CAMMELL LAIRD NORTH | 332742 | 388445
Wirral | CAMMELL LAIRD SOUTH | 332706 | 387556
Wirral | CASTLEFIELDS | 354121 | 382470
Wirral | CEREAL PARTNERS | 335016 | 383545
Wirral | CHAMPION PLUGS | 326966 | 387201
Wirral | CHEMDAL | 332450 | 390571
Wirral | CHESTER GATES | 337854 | 372557
Wirral | CHESTER MAIN | 339210 | 369105
Wirral | CHESTER STREET | 332773 | 388964
Wirral | CHESTER WATER TREATMENT WORKS | 342223 | 363999
Wirral | CHOWLEY | 347294 | 356236
Wirral | CLIFTON | 352363 | 380612
Wirral | COCOA BARRY | 338152 | 366435
Wirral | COUNTESS PARK | 340221 | 368946
Wirral | COW LANE BRIDGE CHTR | 340799 | 366619
Wirral | CRANE BANK | 339837 | 366329
Wirral | CRAVEN STREET | 331446 | 388733
Wirral | CROSTHWAITE AVENUE | 335824 | 379813
Wirral | CROWMERE LANE | 352631 | 374886
Wirral | DARESBURY NPL | 357338 | 383098
Wirral | DARESBURY PARK | 356777 | 381646
Wirral | DEESIDE IND 10TH AVE | 331883 | 371539
Wirral | DEESIDE IND PARK | 332981 | 370838
Wirral | DEESIDE IND PK 6TH AVE | 332346 | 370457
Wirral | DEESIDE PARK | 331043 | 371373
Wirral | DIBBINSDALE | 334045 | 380890
Wirral | DUDDON | 351752 | 365071
Wirral | DUTTON | 355821 | 379614
Wirral | EASTHAM | 334779 | 379290
Wirral | EGERTON | 332123 | 386377
Wirral | EGREMONT | 331868 | 391685
Wirral | ELLESMERE PORT | 341539 | 376288
Wirral | ELTON | 345901 | 375426
Wirral | ENGINEER PARK | 333618 | 367491
Wirral | FLAYBRICK | 329460 | 388998
Wirral | FORD | 327949 | 388250
Wirral | FRODSHAM LOCAL | 351650 | 378056
Wirral | GAYTON | 327876 | 381254
Wirral | GILBROOK DOCK | 330427 | 390116
Wirral | GOWY LANDFILL GEN | 344710 | 371639
Wirral | GPO EXCHANGE | 337180 | 376660
Wirral | GRANGE | 322453 | 387502
Wirral | GREASBY | 324927 | 387174
Wirral | GREAT BOUGHTON | 343161 | 366203
Wirral | GREAT SUTTON | 338605 | 375427
Wirral | GROSVENOR STREET | 340508 | 366064
Wirral | GUILDEN SUTTON | 343651 | 367872
Wirral | H H ROBERTSON THAIN | 340470 | 376319
Wirral | HALTON ROAD | 352362 | 382775
Wirral | HERON BRIDGE | 341169 | 364355
Wirral | HERONS WAY | 339591 | 363071
Wirral | HESWALL | 327076 | 381814
Wirral | HESWALL GRID | 328643 | 381820
Wirral | HIGHER BEBINGTON | 331772 | 385384
Wirral | HILL ROAD | 329471 | 388975
Wirral | HOOLE ROAD-THE ELMS | 341456 | 367293
Wirral | HOOTON MAIN | 334690 | 378196
Wirral | HOOTON PARK 33kV | 338892 | 378349
Wirral | HOPFIELD ROAD | 327012 | 389618
Wirral | HOYLAKE | 321862 | 388779
Wirral | INCE | 345854 | 375857
Wirral | IRBY | 325725 | 384510
Wirral | IRON DISH HELSBY | 349775 | 376117
Wirral | KNUTSFORD WAY | 338833 | 366797
Wirral | LACHE | 338254 | 363972
Wirral | LCWW HUNTINGTON | 342161 | 363981
Wirral | LEASOWE | 327893 | 391817
Wirral | LEDSHAM ROAD | 336888 | 376768
Wirral | LEES LANE | 341542 | 376085
Wirral | LEVER GEORGIA AVENUE | 335246 | 383405
Wirral | LEVER SUNLIGHT | 334129 | 383925
Wirral | LINENHALL STREET | 340302 | 366264
Wirral | LINKSWAY | 329775 | 393434
Wirral | LISCARD | 330679 | 391858
Wirral | LITTLE SUTTON | 337956 | 376776
Wirral | LOWER BEBINGTON | 332571 | 384360
Wirral | MACKAMAX | 353998 | 383518
Wirral | MANNINGS LANE | 342396 | 368121
Wirral | MANOR HILL | 330201 | 388713
Wirral | MANOR PARK | 355346 | 383778
Wirral | MANOR ROAD HOYLAKE | 322265 | 389356
Wirral | MARSHALL STREET | 331376 | 389704
Wirral | MASON STREET RUNCORN | 352138 | 382973
Wirral | MATHER ROAD | 330946 | 388117
Wirral | MBNA | 340259 | 362904
Wirral | MDHB EGERTON DOCK | 332147 | 389602
Wirral | MEOLS | 323275 | 389733
Wirral | MERES EDGE | 348294 | 374885
Wirral | MERSEY ROAD | 351306 | 383235
Wirral | MERSEY WHARF STOR | 335284 | 384320
Wirral | MOBIL OIL | 339100 | 378095
Wirral | MOBIL OIL WALLASEY | 329809 | 390471
Wirral | MOORE | 355793 | 383215
Wirral | MORETON | 326178 | 389877
Wirral | MORGAN REFRACTORIES | 328975 | 378512
Wirral | MORGANITE CERAMICS | 335588 | 381787
Wirral | MURDISHAW | 355886 | 381049
Wirral | NASH KELVINATOR | 335405 | 381985
Wirral | NESTON MAIN | 329760 | 377253
Wirral | NEW ASSOCIATED OCTEL | 341650 | 376287
Wirral | NEW BRIGHTON | 330982 | 393753
Wirral | NEW E PORT LOCAL | 341623 | 376291
Wirral | NEW FERRY | 333625 | 385288
Wirral | NEWTOWN CHESTER | 340585 | 367009
Wirral | NORTHERN BIO POWER | 337422 | 380107
Wirral | NORTHGATE TERRACE | 340438 | 366706
Wirral | NORTHWICH ROAD | 356049 | 379822
Wirral | NORTON CHAINS | 356176 | 383770
Wirral | NWW WOODSIDE 33 | 332739 | 389380
Wirral | NWWA BROMBOROUGH | 334266 | 385109
Wirral | OPTICAL FIBRES | 332559 | 370921
Wirral | OVERCHURCH | 326059 | 388614
Wirral | OXTON | 330058 | 387795
Wirral | PARC ADFER | 331142 | 371490
Wirral | PENSBY | 327370 | 383975
Wirral | PERCIVAL LANE | 349755 | 381979
Wirral | PICOW FARM ROAD | 350803 | 382706
Wirral | PIPERS ASH | 343115 | 367551
Wirral | PLYMYARD | 335577 | 380465
Wirral | POOL LANE | 334532 | 384078
Wirral | POULTON | 330662 | 390462
Wirral | PRENTON 33KV | 329040 | 386748
Wirral | PRENTON LOCAL | 329088 | 386440
Wirral | QUINN GLASS | 345896 | 376446
Wirral | RAF SEALAND | 333495 | 369944
Wirral | ROCK FERRY | 333237 | 385751
Wirral | RUNCORN CENTRAL | 353809 | 381436
Wirral | RUNCORN DOCKS | 349707 | 382018
Wirral | SALTNEY GRID | 337164 | 365316
Wirral | SAUGHALL MASSIE | 325242 | 389214
Wirral | SEACOMBE | 332357 | 390708
Wirral | SEACOMBE VENT SHAFT | 332476 | 390947
Wirral | SEALAND SHOT.ST.WORK | 330995 | 370218
Wirral | SEAVIEW ROAD | 330249 | 392497
Wirral | SHELL OIL SITE ROAD | 342198 | 376364
Wirral | SHELL TRANMERE | 333181 | 387048
Wirral | SHOPPING CITY | 353292 | 381429
Wirral | SHOTWICK | 331398 | 371694
Wirral | SINGLETON AVE 6-6KV | 330998 | 386986
Wirral | SINGLETON AVENUE 11KV | 330996 | 386991
Wirral | SIXTH AVENUE 33KV | 332346 | 370484
Wirral | SMFS KINGSMEADOW | 339992 | 363161
Wirral | SOUTH LISCARD | 331495 | 392343
Wirral | SPILLERS | 330362 | 390111
Wirral | SPITAL | 333047 | 383175
Wirral | STANLOW STOR | 341829 | 376376
Wirral | STATION VIEW | 341721 | 366703
Wirral | STONE MANGANESE | 331323 | 390574
Wirral | STRAWBERRY ROUNDABOUT | 339344 | 373741
Wirral | STRETTON IND ESTATE | 364717 | 383770
Wirral | SUTTON HALL W W B | 337160 | 375538
Wirral | TARPORLEY | 355256 | 361967
Wirral | TARVIN | 349204 | 367252
Wirral | THINGWALL | 326792 | 384914
Wirral | TOMULAR PLACE | 341211 | 366362
Wirral | TOWER WHARF | 340098 | 366748
Wirral | TOYOTA | 331440 | 371167
Wirral | TRANMERE | 332409 | 387765
Wirral | TULIP | 336009 | 382549
Wirral | U.K.F. | 347382 | 376555
Wirral | UML LEVER BROM | 335876 | 383134
Wirral | UNILEVER DUNKIRK | 338118 | 372459
Wirral | UNILEVER RESEARCH | 333534 | 383569
Wirral | UPTON | 327025 | 388077
Wirral | UPTON HEATH | 341658 | 369544
Wirral | VAN LEER NO 1 | 341137 | 376636
Wirral | VAUXHALL NORTH ROAD | 337909 | 379288
Wirral | VAUXHALLS | 337977 | 378761
Wirral | WALBRO | 332178 | 371469
Wirral | WALLASEY GRID | 329939 | 391212
Wirral | WALLASEY VILLAGE | 329012 | 392704
Wirral | WERVIN | 342236 | 370739
Wirral | WEST KIRBY SOUTH | 321794 | 386056
Wirral | WHITBY | 339454 | 375547
Wirral | WIBP HARDKNOTT ROAD | 335418 | 382054
Wirral | WINDMILL HILL 33 | 355795 | 382503
Wirral | WOODCHURCH | 327658 | 386992
Wirral | WOODSIDE | 332727 | 389207
Wirral | YKK | 356284 | 379503